## GES_NBS+CUE
Sequencing | Pump Size ID | Pump Size | Curve | Max flow @ max speed (gpm), 1 pump | Max Branch Flow | Max Header Flow | Number of Active Pumps | Number of Backup Pumps | Number of Total Pumps | Cost Group | Cost Group Type | Suction | Discharge | Branch Minimum | Branch Maximum | Header Minimum | Header Maximum |  |  | Curve | Max flow @ max speed (gpm)
1 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 2 | 0 |  | A | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5 |  | 2 | 2.5 | NBS_012-070_4P_1HP_6.10_SS | 90.8476
2 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 2 | 0 |  | A | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5 |  | 2.5 | 3 | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592
3 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 3 | 4 | NBS_015-070_4P_1HP_5.12_SS | 145.3387
4 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 4 | 5 | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172
5 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 5 | 6 | NBS_015-070_4P_2HP_6.54_SS | 188.3547
6 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 6 | 8 | NBS_015-070_4P_3HP_6.93_SS | 202.4879
7 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 8 | 10 | NBS_015-090_4P_1.5HP_6.69_SS | 102.972
8 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 10 | 12 | NBS_015-090_4P_2HP_7.24_SS | 116.1429
9 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 12 | 14 | NBS_015-090_4P_3HP_8.11_SS | 133.8158
10 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 14 | 16 | NBS_015-090_4P_5HP_9.84_SS | 150.196
11 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 16 | 18 | NBS_015-095_4P_2HP_6.54_SS | 177.561
12 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  | 18 | 20 | NBS_015-095_4P_3HP_7.32_SS | 194.9972
13 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  |  |  | NBS_015-095_4P_5HP_8.82_SS | 230.1371
14 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3 |  |  |  | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034
15 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-095_4P_2HP_5.83_SS | 178.5455
16 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-095_4P_3HP_6.61_SS | 208.9617
17 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-095_4P_5HP_8.11_SS | 260.8895
18 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228
19 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-110_4P_5HP_8.11_SS | 273.669
20 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-110_4P_7.5HP_8.98_SS | 321.881
21 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-110_4P_10HP_9.92_SS | 360.1978
22 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_020-110_4P_15HP_10.31_SS | 376.0572
23 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2 | 3 |  | 4 |  |  |  | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739
24 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2 | 3 |  | 4 |  |  |  | NBS_020-135_4P_10HP_10.16_SS | 299.9456
25 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2 | 3 |  | 4 |  |  |  | NBS_020-135_4P_15HP_11.42_SS | 365.149
26 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2 | 3 |  | 4 |  |  |  | NBS_020-135_4P_20HP_12.52_SS | 403.7936
27 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2 | 3 |  | 4 |  |  |  | NBS_020-135_4P_25HP_13.31_SS | 402.7736
28 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_025-070_4P_1HP_4.65_SS | 183.5282
29 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056
30 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_025-070_4P_2HP_5.83_SS | 254.5738
31 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_025-070_4P_3HP_6.61_SS | 278.649
32 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 2 | 0 |  | A | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3 |  |  |  | NBS_025-070_4P_5HP_6.77_SS | 302.5651
33 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-095_4P_3HP_5.98_SS | 278.138
34 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-095_4P_5HP_7.17_SS | 343.952
35 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817
36 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-095_4P_10HP_9.53_SS | 427.0782
37 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437
38 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-110_4P_10HP_9.45_SS | 422.9151
39 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_025-110_4P_15HP_11.02_SS | 479.4087
40 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997
41 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_030-070_4P_2HP_5.20_SS | 359.467
42 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_030-070_4P_3HP_5.83_SS | 413.6934
43 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 2 | 0 |  | A | NBS_EndSuction | 3 | 2.5 | 3 |  | 4 |  |  |  | NBS_030-070_4P_5HP_6.85_SS | 469.9181
44 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-095_4P_5HP_6.10_SS | 576.7129
45 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666
46 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-095_4P_10HP_7.52_SS | 669.3599
47 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-095_4P_15HP_8.86_SS | 685.5374
48 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-110_4P_10HP_8.35_SS | 487.2856
49 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-110_4P_15HP_9.61_SS | 573.2974
50 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-110_4P_20HP_10.79_SS | 666.5942
51 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-135_4P_15HP_8.98_SS | 598.5182
52 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-135_4P_20HP_9.92_SS | 672.8213
53 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-135_4P_25HP_10.63_SS | 735.3325
54 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-135_4P_30HP_11.26_SS | 787.4175
55 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_030-135_4P_40HP_12.91_SS | 832.83
56 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_040-070_4P_2HP_4.72_SS | 541.7729
57 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_040-070_4P_3HP_5.43_SS | 534.0678
58 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_040-070_4P_5HP_6.30_SS | 695.2568
59 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 2 | 0 |  | A | NBS_EndSuction | 4 | 3 | 4 |  | 5 |  |  |  | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837
60 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628
61 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-095_4P_10HP_7.09_SS | 924.6022
62 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-095_4P_15HP_8.35_SS | 1036.8753
63 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-095_4P_20HP_9.37_SS | 1098.4714
64 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-110_4P_15HP_8.11_SS | 877.0156
65 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-110_4P_20HP_8.74_SS | 948.7162
66 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-110_4P_25HP_9.45_SS | 981.9574
67 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-110_4P_30HP_10.08_SS | 1058.92
68 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-135_4P_20HP_9.29_SS | 812.9455
69 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-135_4P_25HP_10.24_SS | 894.4426
70 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-135_4P_30HP_10.94_SS | 958.5264
71 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-135_4P_40HP_11.81_SS | 1092.3955
72 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-135_4P_50HP_12.83_SS | 1108.1578
73 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_50HP_12.36_SS | 1179.7044
74 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_60HP_13.07_SS | 1257.8884
75 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_75HP_14.02_SS | 1397.6463
76 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_100HP_15.28_SS | 1556.5458
77 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_125HP_16.14_SS | 1658.4722
78 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_040-150_4P_150HP_16.77_SS | 1749.9638
79 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_050-070_4P_3HP_4.88_SS | 840.0118
80 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_050-070_4P_5HP_6.06_SS | 912.3919
81 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895
82 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 2 | 0 |  | A | NBS_EndSuction | 5 | 4 | 5 |  | 6 |  |  |  | NBS_050-070_4P_10HP_6.93_SS | 1003.339
83 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-095_4P_10HP_6.46_SS | 1234.2559
84 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-095_4P_15HP_7.40_SS | 1338.3397
85 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-095_4P_20HP_8.19_SS | 1409.7542
86 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-095_4P_25HP_8.74_SS | 1493.981
87 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-095_4P_30HP_9.13_SS | 1550.69
88 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-110_4P_20HP_8.35_SS | 1352.693
89 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-110_4P_25HP_9.06_SS | 1398.703
90 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-110_4P_30HP_9.61_SS | 1508.9068
91 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-110_4P_40HP_10.63_SS | 1674.3665
92 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_25HP_8.86_SS | 1200.4144
93 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_30HP_9.49_SS | 1283.8269
94 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_40HP_10.59_SS | 1416.7849
95 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_50HP_11.30_SS | 1508.8665
96 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_60HP_12.01_SS | 1598.8017
97 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-135_4P_75HP_13.03_SS | 1689.4197
98 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-150_4P_75HP_11.73_SS | 2092.9884
99 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-150_4P_100HP_12.99_SS | 2346.9884
100 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-150_4P_125HP_14.09_SS | 2529.5219
101 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 2 | 0 |  | A | NBS_EndSuction | 6 | 5 | 6 |  | 8 |  |  |  | NBS_050-150_4P_150HP_14.96_SS | 2703.7978
102 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-095_4P_15HP_7.32_SS | 2169.9766
103 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-095_4P_20HP_7.95_SS | 2284.2526
104 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-095_4P_25HP_8.43_SS | 2385.0423
105 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-095_4P_30HP_8.90_SS | 2493.7612
106 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-095_4P_40HP_9.53_SS | 2617.6301
107 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-110_4P_30HP_8.78_SS | 2227.2787
108 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-110_4P_40HP_9.57_SS | 2407.488
109 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-110_4P_50HP_10.20_SS | 2508.3577
110 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-110_4P_60HP_10.75_SS | 2624.9016
111 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_40HP_9.25_SS | 2111.5713
112 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_50HP_9.96_SS | 2305.4296
113 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_60HP_10.35_SS | 2491.2746
114 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_75HP_11.22_SS | 2766.6299
115 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_100HP_12.24_SS | 3069.239
116 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-135_4P_125HP_12.83_SS | 3426.3556
117 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-150_4P_125HP_11.97_SS | 2867.819
118 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-150_4P_150HP_12.83_SS | 3379.8685
119 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-150_4P_200HP_14.8_SS | 3737.7603
120 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 2 | 0 |  | A | NBS_EndSuction | 8 | 6 | 8 |  | 10 |  |  |  | NBS_060-150_4P_250HP_15.83_SS | 3875.064
121 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-135_4P_60HP_9.84_SS | 4004.1439
122 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-135_4P_75HP_10.31_SS | 4295.2175
123 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-135_4P_100HP_11.26_SS | 4595.0968
124 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-135_4P_125HP_11.89_SS | 4656.6379
125 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-135_4P_150HP_12.60_SS | 4664.6626
126 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-150_4P_125HP_12.20_SS | 3448.9864
127 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-150_4P_150HP_12.99_SS | 3639.5425
128 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-150_4P_200HP_14.25_SS | 4042.4929
129 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 2 | 0 |  | A | NBS_EndSuction | 10 | 8 | 10 |  | 12 |  |  |  | NBS_080-150_4P_250HP_15.59_SS | 4332.4218
130 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 2 | 0 |  | A | NBS_EndSuction | 12 | 10 | 12 |  | 14 |  |  |  | NBS_100-150_4P_150HP_12.48_SS | 5072.7199
131 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 2 | 0 |  | A | NBS_EndSuction | 12 | 10 | 12 |  | 14 |  |  |  | NBS_100-150_4P_200HP_13.66_SS | 5521.0639
132 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 2 | 0 |  | A | NBS_EndSuction | 12 | 10 | 12 |  | 14 |  |  |  | NBS_100-150_4P_250HP_14.76_SS | 5727.2058
133 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 3 | 0 |  | B | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
134 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 3 | 0 |  | B | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
135 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
136 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
137 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
138 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
139 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
140 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
141 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
142 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
143 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
144 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
145 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
146 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
147 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
148 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
149 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
150 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
151 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
152 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
153 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
154 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
155 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2 | 3 |  | 4
156 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2 | 3 |  | 4
157 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2 | 3 |  | 4
158 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2 | 3 |  | 4
159 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2 | 3 |  | 4
160 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
161 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
162 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
163 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
164 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 3 | 0 |  | B | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
165 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
166 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
167 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
168 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
169 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
170 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
171 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
172 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
173 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
174 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
175 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 3 | 0 |  | B | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
176 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
177 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
178 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
179 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
180 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
181 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
182 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
183 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
184 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
185 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
186 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
187 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
188 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
189 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
190 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
191 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 3 | 0 |  | B | NBS_EndSuction | 4 | 3 | 4 |  | 5
192 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
193 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
194 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
195 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
196 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
197 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
198 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
199 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
200 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
201 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
202 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
203 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
204 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
205 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
206 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
207 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
208 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
209 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
210 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
211 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
212 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
213 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
214 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 3 | 0 |  | B | NBS_EndSuction | 5 | 4 | 5 |  | 6
215 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
216 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
217 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
218 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
219 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
220 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
221 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
222 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
223 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
224 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
225 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
226 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
227 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
228 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
229 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
230 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
231 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
232 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
233 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 3 | 0 |  | B | NBS_EndSuction | 6 | 5 | 6 |  | 8
234 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
235 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
236 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
237 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
238 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
239 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
240 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
241 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
242 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
243 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
244 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
245 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
246 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
247 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
248 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
249 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
250 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
251 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
252 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 3 | 0 |  | B | NBS_EndSuction | 8 | 6 | 8 |  | 10
253 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
254 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
255 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
256 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
257 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
258 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
259 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
260 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
261 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 3 | 0 |  | B | NBS_EndSuction | 10 | 8 | 10 |  | 12
262 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 3 | 0 |  | B | NBS_EndSuction | 12 | 10 | 12 |  | 14
263 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 3 | 0 |  | B | NBS_EndSuction | 12 | 10 | 12 |  | 14
264 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 3 | 0 |  | B | NBS_EndSuction | 12 | 10 | 12 |  | 14
265 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 4 | 0 |  | C | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
266 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 4 | 0 |  | C | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
267 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
268 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
269 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
270 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
271 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
272 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
273 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
274 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
275 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
276 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
277 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
278 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
279 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
280 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
281 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
282 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
283 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
284 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
285 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
286 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
287 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2 | 3 |  | 4
288 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2 | 3 |  | 4
289 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2 | 3 |  | 4
290 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2 | 3 |  | 4
291 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2 | 3 |  | 4
292 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
293 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
294 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
295 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
296 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 4 | 0 |  | C | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
297 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
298 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
299 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
300 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
301 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
302 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
303 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
304 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
305 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
306 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
307 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 4 | 0 |  | C | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
308 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
309 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
310 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
311 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
312 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
313 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
314 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
315 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
316 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
317 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
318 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
319 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
320 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
321 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
322 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
323 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 4 | 0 |  | C | NBS_EndSuction | 4 | 3 | 4 |  | 5
324 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
325 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
326 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
327 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
328 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
329 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
330 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
331 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
332 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
333 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
334 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
335 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
336 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
337 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
338 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
339 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
340 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
341 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
342 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
343 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
344 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
345 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
346 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 4 | 0 |  | C | NBS_EndSuction | 5 | 4 | 5 |  | 6
347 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
348 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
349 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
350 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
351 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
352 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
353 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
354 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
355 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
356 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
357 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
358 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
359 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
360 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
361 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
362 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
363 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
364 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
365 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 4 | 0 |  | C | NBS_EndSuction | 6 | 5 | 6 |  | 8
366 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
367 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
368 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
369 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
370 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
371 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
372 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
373 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
374 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
375 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
376 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
377 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
378 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
379 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
380 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
381 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
382 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
383 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
384 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 4 | 0 |  | C | NBS_EndSuction | 8 | 6 | 8 |  | 10
385 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
386 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
387 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
388 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
389 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
390 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
391 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
392 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
393 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 4 | 0 |  | C | NBS_EndSuction | 10 | 8 | 10 |  | 12
394 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 4 | 0 |  | C | NBS_EndSuction | 12 | 10 | 12 |  | 14
395 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 4 | 0 |  | C | NBS_EndSuction | 12 | 10 | 12 |  | 14
396 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 4 | 0 |  | C | NBS_EndSuction | 12 | 10 | 12 |  | 14
397 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 1 | 1 |  | D | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
398 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 1 | 1 |  | D | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
399 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
400 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
401 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
402 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
403 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
404 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
405 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
406 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
407 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
408 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
409 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
410 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
411 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
412 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
413 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
414 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
415 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
416 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
417 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
418 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
419 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2 | 3 |  | 4
420 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2 | 3 |  | 4
421 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2 | 3 |  | 4
422 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2 | 3 |  | 4
423 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2 | 3 |  | 4
424 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
425 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
426 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
427 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
428 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 1 | 1 |  | D | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
429 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
430 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
431 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
432 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
433 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
434 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
435 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
436 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
437 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
438 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
439 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 1 | 1 |  | D | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
440 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
441 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
442 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
443 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
444 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
445 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
446 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
447 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
448 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
449 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
450 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
451 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
452 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
453 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
454 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
455 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 1 | 1 |  | D | NBS_EndSuction | 4 | 3 | 4 |  | 5
456 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
457 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
458 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
459 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
460 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
461 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
462 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
463 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
464 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
465 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
466 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
467 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
468 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
469 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
470 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
471 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
472 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
473 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
474 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
475 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
476 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
477 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
478 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 1 | 1 |  | D | NBS_EndSuction | 5 | 4 | 5 |  | 6
479 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
480 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
481 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
482 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
483 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
484 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
485 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
486 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
487 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
488 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
489 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
490 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
491 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
492 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
493 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
494 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
495 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
496 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
497 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 1 | 1 |  | D | NBS_EndSuction | 6 | 5 | 6 |  | 8
498 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
499 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
500 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
501 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
502 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
503 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
504 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
505 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
506 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
507 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
508 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
509 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
510 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
511 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
512 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
513 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
514 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
515 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
516 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 1 | 1 |  | D | NBS_EndSuction | 8 | 6 | 8 |  | 10
517 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
518 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
519 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
520 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
521 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
522 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
523 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
524 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
525 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 1 | 1 |  | D | NBS_EndSuction | 10 | 8 | 10 |  | 12
526 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 1 | 1 |  | D | NBS_EndSuction | 12 | 10 | 12 |  | 14
527 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 1 | 1 |  | D | NBS_EndSuction | 12 | 10 | 12 |  | 14
528 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 1 | 1 |  | D | NBS_EndSuction | 12 | 10 | 12 |  | 14
529 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 2 | 1 |  | E | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
530 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 2 | 1 |  | E | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
531 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
532 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
533 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
534 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
535 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
536 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
537 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
538 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
539 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
540 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
541 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
542 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
543 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
544 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
545 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
546 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
547 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
548 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
549 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
550 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
551 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2 | 3 |  | 4
552 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2 | 3 |  | 4
553 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2 | 3 |  | 4
554 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2 | 3 |  | 4
555 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2 | 3 |  | 4
556 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
557 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
558 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
559 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
560 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 2 | 1 |  | E | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
561 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
562 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
563 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
564 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
565 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
566 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
567 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
568 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
569 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
570 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
571 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 2 | 1 |  | E | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
572 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
573 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
574 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
575 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
576 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
577 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
578 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
579 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
580 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
581 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
582 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
583 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
584 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
585 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
586 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
587 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 2 | 1 |  | E | NBS_EndSuction | 4 | 3 | 4 |  | 5
588 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
589 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
590 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
591 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
592 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
593 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
594 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
595 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
596 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
597 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
598 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
599 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
600 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
601 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
602 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
603 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
604 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
605 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
606 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
607 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
608 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
609 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
610 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 2 | 1 |  | E | NBS_EndSuction | 5 | 4 | 5 |  | 6
611 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
612 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
613 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
614 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
615 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
616 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
617 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
618 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
619 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
620 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
621 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
622 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
623 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
624 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
625 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
626 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
627 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
628 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
629 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 2 | 1 |  | E | NBS_EndSuction | 6 | 5 | 6 |  | 8
630 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
631 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
632 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
633 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
634 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
635 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
636 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
637 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
638 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
639 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
640 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
641 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
642 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
643 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
644 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
645 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
646 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
647 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
648 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 2 | 1 |  | E | NBS_EndSuction | 8 | 6 | 8 |  | 10
649 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
650 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
651 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
652 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
653 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
654 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
655 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
656 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
657 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 2 | 1 |  | E | NBS_EndSuction | 10 | 8 | 10 |  | 12
658 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 2 | 1 |  | E | NBS_EndSuction | 12 | 10 | 12 |  | 14
659 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 2 | 1 |  | E | NBS_EndSuction | 12 | 10 | 12 |  | 14
660 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 2 | 1 |  | E | NBS_EndSuction | 12 | 10 | 12 |  | 14
661 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 3 | 1 |  | F | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
662 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 3 | 1 |  | F | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
663 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
664 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
665 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
666 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
667 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
668 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
669 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
670 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
671 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
672 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
673 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
674 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
675 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
676 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
677 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
678 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
679 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
680 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
681 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
682 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
683 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2 | 3 |  | 4
684 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2 | 3 |  | 4
685 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2 | 3 |  | 4
686 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2 | 3 |  | 4
687 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2 | 3 |  | 4
688 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
689 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
690 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
691 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
692 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 3 | 1 |  | F | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
693 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
694 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
695 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
696 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
697 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
698 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
699 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
700 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
701 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
702 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
703 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 3 | 1 |  | F | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
704 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
705 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
706 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
707 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
708 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
709 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
710 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
711 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
712 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
713 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
714 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
715 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
716 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
717 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
718 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
719 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 3 | 1 |  | F | NBS_EndSuction | 4 | 3 | 4 |  | 5
720 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
721 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
722 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
723 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
724 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
725 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
726 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
727 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
728 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
729 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
730 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
731 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
732 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
733 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
734 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
735 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
736 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
737 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
738 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
739 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
740 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
741 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
742 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 3 | 1 |  | F | NBS_EndSuction | 5 | 4 | 5 |  | 6
743 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
744 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
745 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
746 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
747 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
748 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
749 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
750 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
751 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
752 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
753 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
754 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
755 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
756 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
757 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
758 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
759 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
760 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
761 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 3 | 1 |  | F | NBS_EndSuction | 6 | 5 | 6 |  | 8
762 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
763 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
764 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
765 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
766 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
767 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
768 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
769 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
770 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
771 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
772 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
773 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
774 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
775 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
776 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
777 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
778 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
779 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
780 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 3 | 1 |  | F | NBS_EndSuction | 8 | 6 | 8 |  | 10
781 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
782 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
783 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
784 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
785 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
786 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
787 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
788 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
789 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 3 | 1 |  | F | NBS_EndSuction | 10 | 8 | 10 |  | 12
790 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 3 | 1 |  | F | NBS_EndSuction | 12 | 10 | 12 |  | 14
791 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 3 | 1 |  | F | NBS_EndSuction | 12 | 10 | 12 |  | 14
792 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 3 | 1 |  | F | NBS_EndSuction | 12 | 10 | 12 |  | 14
793 | 1 | 012-070-4P-1HP | NBS_012-070_4P_1HP_6.10_SS | 90.8476 | 90.8476 |  | 4 | 1 |  | G | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
794 | 2 | 012-070-4P-1pt5HP | NBS_012-070_4P_1.5HP_6.97_SS | 106.5592 | 106.5592 |  | 4 | 1 |  | G | NBS_EndSuction | 2 | 1.25 | 2 |  | 2.5
795 | 3 | 015-070-4P-1HP | NBS_015-070_4P_1HP_5.12_SS | 145.3387 | 145.3387 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
796 | 4 | 015-070-4P-1pt5HP | NBS_015-070_4P_1.5HP_5.91_SS | 167.6172 | 167.6172 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
797 | 5 | 015-070-4P-2HP | NBS_015-070_4P_2HP_6.54_SS | 188.3547 | 188.3547 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
798 | 6 | 015-070-4P-3HP | NBS_015-070_4P_3HP_6.93_SS | 202.4879 | 202.4879 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
799 | 7 | 015-090-4P-1pt5HP | NBS_015-090_4P_1.5HP_6.69_SS | 102.972 | 102.972 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
800 | 8 | 015-090-4P-2HP | NBS_015-090_4P_2HP_7.24_SS | 116.1429 | 116.1429 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
801 | 9 | 015-090-4P-3HP | NBS_015-090_4P_3HP_8.11_SS | 133.8158 | 133.8158 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
802 | 10 | 015-090-4P-5HP | NBS_015-090_4P_5HP_9.84_SS | 150.196 | 150.196 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
803 | 11 | 015-095-4P-2HP | NBS_015-095_4P_2HP_6.54_SS | 177.561 | 177.561 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
804 | 12 | 015-095-4P-3HP | NBS_015-095_4P_3HP_7.32_SS | 194.9972 | 194.9972 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
805 | 13 | 015-095-4P-5HP | NBS_015-095_4P_5HP_8.82_SS | 230.1371 | 230.1371 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
806 | 14 | 015-095-4P-7pt5HP | NBS_015-095_4P_7.5HP_9.84_SS | 242.8034 | 242.8034 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 1.5 | 2.5 |  | 3
807 | 15 | 020-095-4P-2HP | NBS_020-095_4P_2HP_5.83_SS | 178.5455 | 178.5455 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
808 | 16 | 020-095-4P-3HP | NBS_020-095_4P_3HP_6.61_SS | 208.9617 | 208.9617 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
809 | 17 | 020-095-4P-5HP | NBS_020-095_4P_5HP_8.11_SS | 260.8895 | 260.8895 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
810 | 18 | 020-095-4P-7pt5HP | NBS_020-095_4P_7.5HP_9.45_SS | 297.3228 | 297.3228 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
811 | 19 | 020-110-4P-5HP | NBS_020-110_4P_5HP_8.11_SS | 273.669 | 273.669 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
812 | 20 | 020-110-4P-7pt5HP | NBS_020-110_4P_7.5HP_8.98_SS | 321.881 | 321.881 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
813 | 21 | 020-110-4P-10HP | NBS_020-110_4P_10HP_9.92_SS | 360.1978 | 360.1978 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
814 | 22 | 020-110-4P-15HP | NBS_020-110_4P_15HP_10.31_SS | 376.0572 | 376.0572 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
815 | 23 | 020-135-4P-7pt5HP | NBS_020-135_4P_7.5HP_9.29_SS | 261.6739 | 261.6739 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2 | 3 |  | 4
816 | 24 | 020-135-4P-10HP | NBS_020-135_4P_10HP_10.16_SS | 299.9456 | 299.9456 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2 | 3 |  | 4
817 | 25 | 020-135-4P-15HP | NBS_020-135_4P_15HP_11.42_SS | 365.149 | 365.149 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2 | 3 |  | 4
818 | 26 | 020-135-4P-20HP | NBS_020-135_4P_20HP_12.52_SS | 403.7936 | 403.7936 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2 | 3 |  | 4
819 | 27 | 020-135-4P-25HP | NBS_020-135_4P_25HP_13.31_SS | 402.7736 | 402.7736 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2 | 3 |  | 4
820 | 28 | 025-070-4P-1HP | NBS_025-070_4P_1HP_4.65_SS | 183.5282 | 183.5282 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
821 | 29 | 025-070-4P-1pt5HP | NBS_025-070_4P_1.5HP_5.28_SS | 235.9056 | 235.9056 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
822 | 30 | 025-070-4P-2HP | NBS_025-070_4P_2HP_5.83_SS | 254.5738 | 254.5738 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
823 | 31 | 025-070-4P-3HP | NBS_025-070_4P_3HP_6.61_SS | 278.649 | 278.649 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
824 | 32 | 025-070-4P-5HP | NBS_025-070_4P_5HP_6.77_SS | 302.5651 | 302.5651 |  | 4 | 1 |  | G | NBS_EndSuction | 2.5 | 2 | 2.5 |  | 3
825 | 33 | 025-095-4P-3HP | NBS_025-095_4P_3HP_5.98_SS | 278.138 | 278.138 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
826 | 34 | 025-095-4P-5HP | NBS_025-095_4P_5HP_7.17_SS | 343.952 | 343.952 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
827 | 35 | 025-095-4P-7pt5HP | NBS_025-095_4P_7.5HP_8.43_SS | 398.9817 | 398.9817 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
828 | 36 | 025-095-4P-10HP | NBS_025-095_4P_10HP_9.53_SS | 427.0782 | 427.0782 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
829 | 37 | 025-110-4P-7pt5HP | NBS_025-110_4P_7.5HP_8.58_SS | 374.2437 | 374.2437 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
830 | 38 | 025-110-4P-10HP | NBS_025-110_4P_10HP_9.45_SS | 422.9151 | 422.9151 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
831 | 39 | 025-110-4P-15HP | NBS_025-110_4P_15HP_11.02_SS | 479.4087 | 479.4087 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
832 | 40 | 030-070-4P-1pt5HP | NBS_030-070_4P_1.5HP_4.72_SS | 318.8997 | 318.8997 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
833 | 41 | 030-070-4P-2HP | NBS_030-070_4P_2HP_5.20_SS | 359.467 | 359.467 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
834 | 42 | 030-070-4P-3HP | NBS_030-070_4P_3HP_5.83_SS | 413.6934 | 413.6934 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
835 | 43 | 030-070-4P-5HP | NBS_030-070_4P_5HP_6.85_SS | 469.9181 | 469.9181 |  | 4 | 1 |  | G | NBS_EndSuction | 3 | 2.5 | 3 |  | 4
836 | 44 | 030-095-4P-5HP | NBS_030-095_4P_5HP_6.10_SS | 576.7129 | 576.7129 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
837 | 45 | 030-095-4P-7pt5HP | NBS_030-095_4P_7.5HP_6.73_SS | 637.6666 | 637.6666 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
838 | 46 | 030-095-4P-10HP | NBS_030-095_4P_10HP_7.52_SS | 669.3599 | 669.3599 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
839 | 47 | 030-095-4P-15HP | NBS_030-095_4P_15HP_8.86_SS | 685.5374 | 685.5374 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
840 | 48 | 030-110-4P-10HP | NBS_030-110_4P_10HP_8.35_SS | 487.2856 | 487.2856 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
841 | 49 | 030-110-4P-15HP | NBS_030-110_4P_15HP_9.61_SS | 573.2974 | 573.2974 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
842 | 50 | 030-110-4P-20HP | NBS_030-110_4P_20HP_10.79_SS | 666.5942 | 666.5942 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
843 | 51 | 030-135-4P-15HP | NBS_030-135_4P_15HP_8.98_SS | 598.5182 | 598.5182 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
844 | 52 | 030-135-4P-20HP | NBS_030-135_4P_20HP_9.92_SS | 672.8213 | 672.8213 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
845 | 53 | 030-135-4P-25HP | NBS_030-135_4P_25HP_10.63_SS | 735.3325 | 735.3325 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
846 | 54 | 030-135-4P-30HP | NBS_030-135_4P_30HP_11.26_SS | 787.4175 | 787.4175 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
847 | 55 | 030-135-4P-40HP | NBS_030-135_4P_40HP_12.91_SS | 832.83 | 832.83 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
848 | 56 | 040-070-4P-2HP | NBS_040-070_4P_2HP_4.72_SS | 541.7729 | 541.7729 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
849 | 57 | 040-070-4P-3HP | NBS_040-070_4P_3HP_5.43_SS | 534.0678 | 534.0678 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
850 | 58 | 040-070-4P-5HP | NBS_040-070_4P_5HP_6.30_SS | 695.2568 | 695.2568 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
851 | 59 | 040-070-4P-7pt5HP | NBS_040-070_4P_7.5HP_6.85_SS | 724.1837 | 724.1837 |  | 4 | 1 |  | G | NBS_EndSuction | 4 | 3 | 4 |  | 5
852 | 60 | 040-095-4P-7pt5HP | NBS_040-095_4P_7.5HP_6.38_SS | 864.0628 | 864.0628 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
853 | 61 | 040-095-4P-10HP | NBS_040-095_4P_10HP_7.09_SS | 924.6022 | 924.6022 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
854 | 62 | 040-095-4P-15HP | NBS_040-095_4P_15HP_8.35_SS | 1036.8753 | 1036.8753 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
855 | 63 | 040-095-4P-20HP | NBS_040-095_4P_20HP_9.37_SS | 1098.4714 | 1098.4714 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
856 | 64 | 040-110-4P-15HP | NBS_040-110_4P_15HP_8.11_SS | 877.0156 | 877.0156 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
857 | 65 | 040-110-4P-20HP | NBS_040-110_4P_20HP_8.74_SS | 948.7162 | 948.7162 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
858 | 66 | 040-110-4P-25HP | NBS_040-110_4P_25HP_9.45_SS | 981.9574 | 981.9574 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
859 | 67 | 040-110-4P-30HP | NBS_040-110_4P_30HP_10.08_SS | 1058.92 | 1058.92 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
860 | 68 | 040-135-4P-20HP | NBS_040-135_4P_20HP_9.29_SS | 812.9455 | 812.9455 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
861 | 69 | 040-135-4P-25HP | NBS_040-135_4P_25HP_10.24_SS | 894.4426 | 894.4426 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
862 | 70 | 040-135-4P-30HP | NBS_040-135_4P_30HP_10.94_SS | 958.5264 | 958.5264 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
863 | 71 | 040-135-4P-40HP | NBS_040-135_4P_40HP_11.81_SS | 1092.3955 | 1092.3955 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
864 | 72 | 040-135-4P-50HP | NBS_040-135_4P_50HP_12.83_SS | 1108.1578 | 1108.1578 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
865 | 73 | 040-150-4P-50HP | NBS_040-150_4P_50HP_12.36_SS | 1179.7044 | 1179.7044 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
866 | 74 | 040-150-4P-60HP | NBS_040-150_4P_60HP_13.07_SS | 1257.8884 | 1257.8884 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
867 | 75 | 040-150-4P-75HP | NBS_040-150_4P_75HP_14.02_SS | 1397.6463 | 1397.6463 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
868 | 76 | 040-150-4P-100HP | NBS_040-150_4P_100HP_15.28_SS | 1556.5458 | 1556.5458 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
869 | 77 | 040-150-4P-125HP | NBS_040-150_4P_125HP_16.14_SS | 1658.4722 | 1658.4722 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
870 | 78 | 040-150-4P-150HP | NBS_040-150_4P_150HP_16.77_SS | 1749.9638 | 1749.9638 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
871 | 79 | 050-070-4P-3HP | NBS_050-070_4P_3HP_4.88_SS | 840.0118 | 840.0118 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
872 | 80 | 050-070-4P-5HP | NBS_050-070_4P_5HP_6.06_SS | 912.3919 | 912.3919 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
873 | 81 | 050-070-4P-7pt5HP | NBS_050-070_4P_7.5HP_6.61_SS | 963.4895 | 963.4895 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
874 | 82 | 050-070-4P-10HP | NBS_050-070_4P_10HP_6.93_SS | 1003.339 | 1003.339 |  | 4 | 1 |  | G | NBS_EndSuction | 5 | 4 | 5 |  | 6
875 | 83 | 050-095-4P-10HP | NBS_050-095_4P_10HP_6.46_SS | 1234.2559 | 1234.2559 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
876 | 84 | 050-095-4P-15HP | NBS_050-095_4P_15HP_7.40_SS | 1338.3397 | 1338.3397 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
877 | 85 | 050-095-4P-20HP | NBS_050-095_4P_20HP_8.19_SS | 1409.7542 | 1409.7542 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
878 | 86 | 050-095-4P-25HP | NBS_050-095_4P_25HP_8.74_SS | 1493.981 | 1493.981 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
879 | 87 | 050-095-4P-30HP | NBS_050-095_4P_30HP_9.13_SS | 1550.69 | 1550.69 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
880 | 88 | 050-110-4P-20HP | NBS_050-110_4P_20HP_8.35_SS | 1352.693 | 1352.693 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
881 | 89 | 050-110-4P-25HP | NBS_050-110_4P_25HP_9.06_SS | 1398.703 | 1398.703 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
882 | 90 | 050-110-4P-30HP | NBS_050-110_4P_30HP_9.61_SS | 1508.9068 | 1508.9068 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
883 | 91 | 050-110-4P-40HP | NBS_050-110_4P_40HP_10.63_SS | 1674.3665 | 1674.3665 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
884 | 92 | 050-135-4P-25HP | NBS_050-135_4P_25HP_8.86_SS | 1200.4144 | 1200.4144 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
885 | 93 | 050-135-4P-30HP | NBS_050-135_4P_30HP_9.49_SS | 1283.8269 | 1283.8269 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
886 | 94 | 050-135-4P-40HP | NBS_050-135_4P_40HP_10.59_SS | 1416.7849 | 1416.7849 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
887 | 95 | 050-135-4P-50HP | NBS_050-135_4P_50HP_11.30_SS | 1508.8665 | 1508.8665 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
888 | 96 | 050-135-4P-60HP | NBS_050-135_4P_60HP_12.01_SS | 1598.8017 | 1598.8017 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
889 | 97 | 050-135-4P-75HP | NBS_050-135_4P_75HP_13.03_SS | 1689.4197 | 1689.4197 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
890 | 98 | 050-150-4P-75HP | NBS_050-150_4P_75HP_11.73_SS | 2092.9884 | 2092.9884 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
891 | 99 | 050-150-4P-100HP | NBS_050-150_4P_100HP_12.99_SS | 2346.9884 | 2346.9884 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
892 | 100 | 050-150-4P-125HP | NBS_050-150_4P_125HP_14.09_SS | 2529.5219 | 2529.5219 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
893 | 101 | 050-150-4P-150HP | NBS_050-150_4P_150HP_14.96_SS | 2703.7978 | 2703.7978 |  | 4 | 1 |  | G | NBS_EndSuction | 6 | 5 | 6 |  | 8
894 | 102 | 060-095-4P-15HP | NBS_060-095_4P_15HP_7.32_SS | 2169.9766 | 2169.9766 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
895 | 103 | 060-095-4P-20HP | NBS_060-095_4P_20HP_7.95_SS | 2284.2526 | 2284.2526 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
896 | 104 | 060-095-4P-25HP | NBS_060-095_4P_25HP_8.43_SS | 2385.0423 | 2385.0423 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
897 | 105 | 060-095-4P-30HP | NBS_060-095_4P_30HP_8.90_SS | 2493.7612 | 2493.7612 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
898 | 106 | 060-095-4P-40HP | NBS_060-095_4P_40HP_9.53_SS | 2617.6301 | 2617.6301 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
899 | 107 | 060-110-4P-30HP | NBS_060-110_4P_30HP_8.78_SS | 2227.2787 | 2227.2787 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
900 | 108 | 060-110-4P-40HP | NBS_060-110_4P_40HP_9.57_SS | 2407.488 | 2407.488 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
901 | 109 | 060-110-4P-50HP | NBS_060-110_4P_50HP_10.20_SS | 2508.3577 | 2508.3577 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
902 | 110 | 060-110-4P-60HP | NBS_060-110_4P_60HP_10.75_SS | 2624.9016 | 2624.9016 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
903 | 111 | 060-135-4P-40HP | NBS_060-135_4P_40HP_9.25_SS | 2111.5713 | 2111.5713 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
904 | 112 | 060-135-4P-50HP | NBS_060-135_4P_50HP_9.96_SS | 2305.4296 | 2305.4296 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
905 | 113 | 060-135-4P-60HP | NBS_060-135_4P_60HP_10.35_SS | 2491.2746 | 2491.2746 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
906 | 114 | 060-135-4P-75HP | NBS_060-135_4P_75HP_11.22_SS | 2766.6299 | 2766.6299 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
907 | 115 | 060-135-4P-100HP | NBS_060-135_4P_100HP_12.24_SS | 3069.239 | 3069.239 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
908 | 116 | 060-135-4P-125HP | NBS_060-135_4P_125HP_12.83_SS | 3426.3556 | 3426.3556 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
909 | 117 | 060-150-4P-125HP | NBS_060-150_4P_125HP_11.97_SS | 2867.819 | 2867.819 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
910 | 118 | 060-150-4P-150HP | NBS_060-150_4P_150HP_12.83_SS | 3379.8685 | 3379.8685 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
911 | 119 | 060-150-4P-200HP | NBS_060-150_4P_200HP_14.8_SS | 3737.7603 | 3737.7603 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
912 | 120 | 060-150-4P-250HP | NBS_060-150_4P_250HP_15.83_SS | 3875.064 | 3875.064 |  | 4 | 1 |  | G | NBS_EndSuction | 8 | 6 | 8 |  | 10
913 | 121 | 080-135-4P-60HP | NBS_080-135_4P_60HP_9.84_SS | 4004.1439 | 4004.1439 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
914 | 122 | 080-135-4P-75HP | NBS_080-135_4P_75HP_10.31_SS | 4295.2175 | 4295.2175 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
915 | 123 | 080-135-4P-100HP | NBS_080-135_4P_100HP_11.26_SS | 4595.0968 | 4595.0968 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
916 | 124 | 080-135-4P-125HP | NBS_080-135_4P_125HP_11.89_SS | 4656.6379 | 4656.6379 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
917 | 125 | 080-135-4P-150HP | NBS_080-135_4P_150HP_12.60_SS | 4664.6626 | 4664.6626 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
918 | 126 | 080-150-4P-125HP | NBS_080-150_4P_125HP_12.20_SS | 3448.9864 | 3448.9864 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
919 | 127 | 080-150-4P-150HP | NBS_080-150_4P_150HP_12.99_SS | 3639.5425 | 3639.5425 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
920 | 128 | 080-150-4P-200HP | NBS_080-150_4P_200HP_14.25_SS | 4042.4929 | 4042.4929 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
921 | 129 | 080-150-4P-250HP | NBS_080-150_4P_250HP_15.59_SS | 4332.4218 | 4332.4218 |  | 4 | 1 |  | G | NBS_EndSuction | 10 | 8 | 10 |  | 12
922 | 130 | 100-150-4P-150HP | NBS_100-150_4P_150HP_12.48_SS | 5072.7199 | 5072.7199 |  | 4 | 1 |  | G | NBS_EndSuction | 12 | 10 | 12 |  | 14
923 | 131 | 100-150-4P-200HP | NBS_100-150_4P_200HP_13.66_SS | 5521.0639 | 5521.0639 |  | 4 | 1 |  | G | NBS_EndSuction | 12 | 10 | 12 |  | 14
924 | 132 | 100-150-4P-250HP | NBS_100-150_4P_250HP_14.76_SS | 5727.2058 | 5727.2058 |  | 4 | 1 |  | G | NBS_EndSuction | 12 | 10 | 12 |  | 14

## Max flow to diameter
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.) | Flow (gpm) | Pipe Diameter (in.)
90.8476 | 2.5 | 181.6952 | 3 | 20 | 2
106.5592 | 2.5 | 213.1183 | 3 | 25 | 2
145.3387 |  | 290.6773 |  | 30 | 2
167.6172 |  | 335.2343 |  | 35 | 2
188.3547 |  | 376.7094 |  | 40 | 2
202.4879 |  | 404.9758 |  | 45 | 2
102.972 |  | 205.9439 |  | 50 | 2
116.1429 |  | 232.2859 |  | 55 | 2
133.8158 |  | 267.6317 |  | 60 | 2
150.196 |  | 300.3921 |  | 65 | 2
177.561 |  | 355.122 |  | 70 | 2
194.9972 |  | 389.9945 |  | 75 | 2
230.1371 |  | 460.2742 |  | 80 | 2
242.8034 |  | 485.6067 |  | 85 | 2.5
178.5455 |  | 357.091 |  | 90 | 2.5
208.9617 |  | 417.9234 |  | 95 | 2.5
260.8895 |  | 521.7789 |  | 100 | 2.5
297.3228 |  | 594.6456 |  | 105 | 2.5
273.669 |  | 547.3381 |  | 110 | 2.5
321.881 |  | 643.7619 |  | 115 | 2.5
360.1978 |  | 720.3955 |  | 120 | 2.5
376.0572 |  | 752.1143 |  | 125 | 3
261.6739 |  | 523.3477 |  | 130 | 3
299.9456 |  | 599.8912 |  | 135 | 3
365.149 |  | 730.298 |  | 140 | 3
403.7936 |  | 807.5873 |  | 145 | 3
402.7736 |  | 805.5473 |  | 150 | 3
183.5282 |  | 367.0563 |  | 155 | 3
235.9056 |  | 471.8113 |  | 160 | 3
254.5738 |  | 509.1476 |  | 165 | 3
278.649 |  | 557.2981 |  | 170 | 3
302.5651 |  | 605.1301 |  | 175 | 3
278.138 |  | 556.2759 |  | 180 | 3
343.952 |  | 687.904 |  | 185 | 3
398.9817 |  | 797.9634 |  | 190 | 3
427.0782 |  | 854.1563 |  | 195 | 3
374.2437 |  | 748.4875 |  | 200 | 3
422.9151 |  | 845.8302 |  | 205 | 3
479.4087 |  | 958.8173 |  | 210 | 3
318.8997 |  | 637.7994 |  | 215 | 4
359.467 |  | 718.934 |  | 220 | 4
413.6934 |  | 827.3869 |  | 225 | 4
469.9181 |  | 939.8361 |  | 230 | 4
576.7129 |  | 1153.4258 |  | 235 | 4
637.6666 |  | 1275.3332 |  | 240 | 4
669.3599 |  | 1338.7198 |  | 245 | 4
685.5374 |  | 1371.0747 |  | 250 | 4
487.2856 |  | 974.5712 |  | 255 | 4
573.2974 |  | 1146.5948 |  | 260 | 4
666.5942 |  | 1333.1883 |  | 265 | 4
598.5182 |  | 1197.0364 |  | 270 | 4
672.8213 |  | 1345.6425 |  | 275 | 4
735.3325 |  | 1470.665 |  | 280 | 4
787.4175 |  | 1574.835 |  | 285 | 4
832.83 |  | 1665.66 |  | 290 | 4
541.7729 |  | 1083.5457 |  | 295 | 4
534.0678 |  | 1068.1357 |  | 300 | 4
695.2568 |  | 1390.5137 |  | 305 | 4
724.1837 |  | 1448.3673 |  | 310 | 4
864.0628 |  | 1728.1255 |  | 315 | 4
924.6022 |  | 1849.2044 |  | 320 | 4
1036.8753 |  | 2073.7507 |  | 325 | 4
1098.4714 |  | 2196.9429 |  | 330 | 4
877.0156 |  | 1754.0312 |  | 335 | 4
948.7162 |  | 1897.4325 |  | 340 | 4
981.9574 |  | 1963.9148 |  | 345 | 4
1058.92 |  | 2117.8401 |  | 350 | 4
812.9455 |  | 1625.891 |  | 355 | 4
894.4426 |  | 1788.8851 |  | 360 | 4
958.5264 |  | 1917.0528 |  | 365 | 4
1092.3955 |  | 2184.791 |  | 370 | 4
1108.1578 |  | 2216.3155 |  | 375 | 4
1179.7044 |  | 2359.4087 |  | 380 | 4
1257.8884 |  | 2515.7767 |  | 385 | 4
1397.6463 |  | 2795.2926 |  | 390 | 4
1556.5458 |  | 3113.0916 |  | 395 | 4
1658.4722 |  | 3316.9444 |  | 400 | 5
1749.9638 |  | 3499.9275 |  | 450 | 5
840.0118 |  | 1680.0235 |  | 500 | 5
912.3919 |  | 1824.7838 |  | 550 | 5
963.4895 |  | 1926.979 |  | 600 | 5
1003.339 |  | 2006.678 |  | 650 | 6
1234.2559 |  | 2468.5118 |  | 700 | 6
1338.3397 |  | 2676.6794 |  | 750 | 6
1409.7542 |  | 2819.5084 |  | 800 | 6
1493.981 |  | 2987.9621 |  | 850 | 6
1550.69 |  | 3101.38 |  | 900 | 6
1352.693 |  | 2705.3861 |  | 950 | 8
1398.703 |  | 2797.406 |  | 1000 | 8
1508.9068 |  | 3017.8135 |  | 1050 | 8
1674.3665 |  | 3348.7331 |  | 1100 | 8
1200.4144 |  | 2400.8289 |  | 1150 | 8
1283.8269 |  | 2567.6538 |  | 1200 | 8
1416.7849 |  | 2833.5698 |  | 1250 | 8
1508.8665 |  | 3017.733 |  | 1300 | 8
1598.8017 |  | 3197.6035 |  | 1350 | 8
1689.4197 |  | 3378.8394 |  | 1400 | 8
2092.9884 |  | 4185.9767 |  | 1450 | 8
2346.9884 |  | 4693.9769 |  | 1500 | 8
2529.5219 |  | 5059.0437 |  | 1550 | 8
2703.7978 |  | 5407.5955 |  | 1600 | 10
2169.9766 |  | 4339.9531 |  | 1650 | 10
2284.2526 |  | 4568.5051 |  | 1700 | 10
2385.0423 |  | 4770.0846 |  | 1750 | 10
2493.7612 |  | 4987.5224 |  | 1800 | 10
2617.6301 |  | 5235.2602 |  | 1850 | 10
2227.2787 |  | 4454.5573 |  | 1900 | 10
2407.488 |  | 4814.9761 |  | 1950 | 10
2508.3577 |  | 5016.7154 |  | 2000 | 10
2624.9016 |  | 5249.8033 |  | 2050 | 10
2111.5713 |  | 4223.1426 |  | 2100 | 10
2305.4296 |  | 4610.8591 |  | 2150 | 10
2491.2746 |  | 4982.5492 |  | 2200 | 10
2766.6299 |  | 5533.2599 |  | 2250 | 10
3069.239 |  | 6138.4781 |  | 2300 | 10
3426.3556 |  | 6852.7113 |  | 2350 | 10
2867.819 |  | 5735.638 |  | 2400 | 10
3379.8685 |  | 6759.737 |  | 2450 | 10
3737.7603 |  | 7475.5206 |  | 2500 | 12
3875.064 |  | 7750.128 |  | 2550 | 12
4004.1439 |  | 8008.2879 |  | 2600 | 12
4295.2175 |  | 8590.4351 |  | 2650 | 12
4595.0968 |  | 9190.1937 |  | 2700 | 12
4656.6379 |  | 9313.2758 |  | 2750 | 12
4664.6626 |  | 9329.3252 |  | 2800 | 12
3448.9864 |  | 6897.9727 |  | 2850 | 12
3639.5425 |  | 7279.085 |  | 2900 | 12
4042.4929 |  | 8084.9858 |  | 2950 | 12
4332.4218 |  | 8664.8435 |  | 3000 | 12
5072.7199 |  | 10145.4398 |  | 3050 | 12
5521.0639 |  | 11042.1279 |  | 3100 | 12
5727.2058 |  | 11454.4117 |  | 3150 | 12
90.8476 |  | 272.5428 |  | 3200 | 12
106.5592 |  | 319.6775 |  | 3250 | 12
145.3387 |  | 436.016 |  | 3300 | 12
167.6172 |  | 502.8515 |  | 3350 | 12
188.3547 |  | 565.064 |  | 3400 | 12
202.4879 |  | 607.4636 |  | 3450 | 12
102.972 |  | 308.9159 |  | 3500 | 12
116.1429 |  | 348.4288 |  | 3550 | 14
133.8158 |  | 401.4475 |  | 3600 | 14
150.196 |  | 450.5881 |  | 3650 | 14
177.561 |  | 532.683 |  | 3700 | 14
194.9972 |  | 584.9917 |  | 3750 | 14
230.1371 |  | 690.4113 |  | 3800 | 14
242.8034 |  | 728.4101 |  | 3850 | 14
178.5455 |  | 535.6365 |  | 3900 | 14
208.9617 |  | 626.885 |  | 3950 | 14
260.8895 |  | 782.6684 |  | 4000 | 14
297.3228 |  | 891.9684 |  | 4050 | 14
273.669 |  | 821.0071 |  | 4100 | 14
321.881 |  | 965.6429 |  | 4150 | 14
360.1978 |  | 1080.5933 |  | 4200 | 14
376.0572 |  | 1128.1715 |  | 4250 | 16
261.6739 |  | 785.0216 |  | 4300 | 16
299.9456 |  | 899.8369 |  | 4350 | 16
365.149 |  | 1095.4471 |  | 4400 | 16
403.7936 |  | 1211.3809 |  | 4450 | 16
402.7736 |  | 1208.3209 |  | 4500 | 16
183.5282 |  | 550.5845 |  | 4550 | 16
235.9056 |  | 707.7169 |  | 4600 | 16
254.5738 |  | 763.7214 |  | 4650 | 16
278.649 |  | 835.9471 |  | 4700 | 16
302.5651 |  | 907.6952 |  | 4750 | 16
278.138 |  | 834.4139 |  | 4800 | 16
343.952 |  | 1031.8561 |  | 4850 | 16
398.9817 |  | 1196.9451 |  | 4900 | 16
427.0782 |  | 1281.2345 |  | 4950 | 16
374.2437 |  | 1122.7312 |  | 5000 | 16
422.9151 |  | 1268.7454 |  | 5050 | 16
479.4087 |  | 1438.226 |  | 5100 | 16
318.8997 |  | 956.6991 |  | 5150 | 16
359.467 |  | 1078.4011 |  | 5200 | 16
413.6934 |  | 1241.0803 |  | 5250 | 16
469.9181 |  | 1409.7542 |  | 5300 | 16
576.7129 |  | 1730.1386 |  | 5350 | 16
637.6666 |  | 1912.9998 |  | 5400 | 16
669.3599 |  | 2008.0797 |  | 5450 | 16
685.5374 |  | 2056.6121 |  | 5500 | 16
487.2856 |  | 1461.8568 |  | 5550 | 18
573.2974 |  | 1719.8922 |  | 5600 | 18
666.5942 |  | 1999.7825 |  | 5650 | 18
598.5182 |  | 1795.5546 |  | 5700 | 18
672.8213 |  | 2018.4638 |  | 5750 | 18
735.3325 |  | 2205.9974 |  | 5800 | 18
787.4175 |  | 2362.2524 |  | 5850 | 18
832.83 |  | 2498.4899 |  | 6000 | 18
541.7729 |  | 1625.3186 |  | 6150 | 18
534.0678 |  | 1602.2035 |  | 6300 | 18
695.2568 |  | 2085.7705 |  | 6450 | 18
724.1837 |  | 2172.551 |  | 6600 | 18
864.0628 |  | 2592.1883 |  | 6750 | 18
924.6022 |  | 2773.8066 |  | 6900 | 18
1036.8753 |  | 3110.626 |  | 7050 | 20
1098.4714 |  | 3295.4143 |  | 7200 | 20
877.0156 |  | 2631.0468 |  | 7350 | 20
948.7162 |  | 2846.1487 |  | 7500 | 20
981.9574 |  | 2945.8722 |  | 7650 | 20
1058.92 |  | 3176.7601 |  | 7800 | 20
812.9455 |  | 2438.8364 |  | 7950 | 20
894.4426 |  | 2683.3277 |  | 8100 | 20
958.5264 |  | 2875.5792 |  | 8250 | 20
1092.3955 |  | 3277.1865 |  | 8400 | 20
1108.1578 |  | 3324.4733 |  | 8550 | 20
1179.7044 |  | 3539.1131 |  | 8700 | 20
1257.8884 |  | 3773.6651 |  | 8850 | 24
1397.6463 |  | 4192.9389 |  | 9000 | 24
1556.5458 |  | 4669.6374 |  | 9150 | 24
1658.4722 |  | 4975.4165 |  | 9300 | 24
1749.9638 |  | 5249.8913 |  | 9450 | 24
840.0118 |  | 2520.0353 |  | 9600 | 24
912.3919 |  | 2737.1757 |  | 9750 | 24
963.4895 |  | 2890.4686 |  | 9900 | 24
1003.339 |  | 3010.017 |  | 10050 | 24
1234.2559 |  | 3702.7677 |  | 10200 | 24
1338.3397 |  | 4015.019 |  | 10350 | 24
1409.7542 |  | 4229.2626 |  | 10500 | 24
1493.981 |  | 4481.9431 |  | 10650 | 24
1550.69 |  | 4652.0699 |  | 10800 | 24
1352.693 |  | 4058.0791 |  | 10950 | 24
1398.703 |  | 4196.109 |  | 11100 | 24
1508.9068 |  | 4526.7203 |  | 11250 | 24
1674.3665 |  | 5023.0996 |  | 11400 | 24
1200.4144 |  | 3601.2433 |  | 11550 | 24
1283.8269 |  | 3851.4807 |  | 11700 | 24
1416.7849 |  | 4250.3547 |  | 11850 | 24
1508.8665 |  | 4526.5994 |  | 12000 | 24
1598.8017 |  | 4796.4052 |  | 12150 | 24
1689.4197 |  | 5068.259 |  | 12300 | 24
2092.9884 |  | 6278.9651 |  | 12450 | 24
2346.9884 |  | 7040.9653 |  | 12600 | 24
2529.5219 |  | 7588.5656
2703.7978 |  | 8111.3933
2169.9766 |  | 6509.9297
2284.2526 |  | 6852.7577
2385.0423 |  | 7155.1269
2493.7612 |  | 7481.2836
2617.6301 |  | 7852.8904
2227.2787 |  | 6681.836
2407.488 |  | 7222.4641
2508.3577 |  | 7525.0732
2624.9016 |  | 7874.7049
2111.5713 |  | 6334.7139
2305.4296 |  | 6916.2887
2491.2746 |  | 7473.8238
2766.6299 |  | 8299.8898
3069.239 |  | 9207.7171
3426.3556 |  | 10279.0669
2867.819 |  | 8603.4569
3379.8685 |  | 10139.6056
3737.7603 |  | 11213.2809
3875.064 |  | 11625.1919
4004.1439 |  | 12012.4318
4295.2175 |  | 12885.6526
4595.0968 |  | 13785.2905
4656.6379 |  | 13969.9138
4664.6626 |  | 13993.9878
3448.9864 |  | 10346.9591
3639.5425 |  | 10918.6274
4042.4929 |  | 12127.4788
4332.4218 |  | 12997.2653
5072.7199 |  | 15218.1598
5521.0639 |  | 16563.1918
5727.2058 |  | 17181.6175
90.8476 |  | 363.3904
106.5592 |  | 426.2366
145.3387 |  | 581.3546
167.6172 |  | 670.4687
188.3547 |  | 753.4187
202.4879 |  | 809.9515
102.972 |  | 411.8879
116.1429 |  | 464.5717
133.8158 |  | 535.2633
150.196 |  | 600.7841
177.561 |  | 710.244
194.9972 |  | 779.989
230.1371 |  | 920.5484
242.8034 |  | 971.2134
178.5455 |  | 714.1819
208.9617 |  | 835.8467
260.8895 |  | 1043.5578
297.3228 |  | 1189.2912
273.669 |  | 1094.6762
321.881 |  | 1287.5239
360.1978 |  | 1440.7911
376.0572 |  | 1504.2286
261.6739 |  | 1046.6955
299.9456 |  | 1199.7825
365.149 |  | 1460.5961
403.7936 |  | 1615.1746
402.7736 |  | 1611.0945
183.5282 |  | 734.1127
235.9056 |  | 943.6226
254.5738 |  | 1018.2952
278.649 |  | 1114.5962
302.5651 |  | 1210.2603
278.138 |  | 1112.5518
343.952 |  | 1375.8081
398.9817 |  | 1595.9268
427.0782 |  | 1708.3126
374.2437 |  | 1496.975
422.9151 |  | 1691.6605
479.4087 |  | 1917.6347
318.8997 |  | 1275.5988
359.467 |  | 1437.8681
413.6934 |  | 1654.7738
469.9181 |  | 1879.6723
576.7129 |  | 2306.8515
637.6666 |  | 2550.6665
669.3599 |  | 2677.4396
685.5374 |  | 2742.1495
487.2856 |  | 1949.1425
573.2974 |  | 2293.1896
666.5942 |  | 2666.3766
598.5182 |  | 2394.0728
672.8213 |  | 2691.2851
735.3325 |  | 2941.3299
787.4175 |  | 3149.6699
832.83 |  | 3331.3199
541.7729 |  | 2167.0915
534.0678 |  | 2136.2714
695.2568 |  | 2781.0273
724.1837 |  | 2896.7347
864.0628 |  | 3456.2511
924.6022 |  | 3698.4088
1036.8753 |  | 4147.5013
1098.4714 |  | 4393.8858
877.0156 |  | 3508.0625
948.7162 |  | 3794.8649
981.9574 |  | 3927.8296
1058.92 |  | 4235.6802
812.9455 |  | 3251.7819
894.4426 |  | 3577.7702
958.5264 |  | 3834.1056
1092.3955 |  | 4369.582
1108.1578 |  | 4432.631
1179.7044 |  | 4718.8174
1257.8884 |  | 5031.5535
1397.6463 |  | 5590.5852
1556.5458 |  | 6226.1832
1658.4722 |  | 6633.8887
1749.9638 |  | 6999.8551
840.0118 |  | 3360.047
912.3919 |  | 3649.5676
963.4895 |  | 3853.9581
1003.339 |  | 4013.356
1234.2559 |  | 4937.0235
1338.3397 |  | 5353.3587
1409.7542 |  | 5639.0168
1493.981 |  | 5975.9242
1550.69 |  | 6202.7599
1352.693 |  | 5410.7721
1398.703 |  | 5594.812
1508.9068 |  | 6035.6271
1674.3665 |  | 6697.4661
1200.4144 |  | 4801.6577
1283.8269 |  | 5135.3076
1416.7849 |  | 5667.1396
1508.8665 |  | 6035.4659
1598.8017 |  | 6395.207
1689.4197 |  | 6757.6787
2092.9884 |  | 8371.9535
2346.9884 |  | 9387.9538
2529.5219 |  | 10118.0875
2703.7978 |  | 10815.191
2169.9766 |  | 8679.9063
2284.2526 |  | 9137.0102
2385.0423 |  | 9540.1692
2493.7612 |  | 9975.0448
2617.6301 |  | 10470.5205
2227.2787 |  | 8909.1146
2407.488 |  | 9629.9521
2508.3577 |  | 10033.4309
2624.9016 |  | 10499.6065
2111.5713 |  | 8446.2852
2305.4296 |  | 9221.7182
2491.2746 |  | 9965.0984
2766.6299 |  | 11066.5198
3069.239 |  | 12276.9561
3426.3556 |  | 13705.4225
2867.819 |  | 11471.2759
3379.8685 |  | 13519.4741
3737.7603 |  | 14951.0411
3875.064 |  | 15500.2559
4004.1439 |  | 16016.5758
4295.2175 |  | 17180.8701
4595.0968 |  | 18380.3874
4656.6379 |  | 18626.5517
4664.6626 |  | 18658.6504
3448.9864 |  | 13795.9455
3639.5425 |  | 14558.1699
4042.4929 |  | 16169.9717
4332.4218 |  | 17329.687
5072.7199 |  | 20290.8797
5521.0639 |  | 22084.2557
5727.2058 |  | 22908.8234
90.8476 |  | 90.8476
106.5592 |  | 106.5592
145.3387 |  | 145.3387
167.6172 |  | 167.6172
188.3547 |  | 188.3547
202.4879 |  | 202.4879
102.972 |  | 102.972
116.1429 |  | 116.1429
133.8158 |  | 133.8158
150.196 |  | 150.196
177.561 |  | 177.561
194.9972 |  | 194.9972
230.1371 |  | 230.1371
242.8034 |  | 242.8034
178.5455 |  | 178.5455
208.9617 |  | 208.9617
260.8895 |  | 260.8895
297.3228 |  | 297.3228
273.669 |  | 273.669
321.881 |  | 321.881
360.1978 |  | 360.1978
376.0572 |  | 376.0572
261.6739 |  | 261.6739
299.9456 |  | 299.9456
365.149 |  | 365.149
403.7936 |  | 403.7936
402.7736 |  | 402.7736
183.5282 |  | 183.5282
235.9056 |  | 235.9056
254.5738 |  | 254.5738
278.649 |  | 278.649
302.5651 |  | 302.5651
278.138 |  | 278.138
343.952 |  | 343.952
398.9817 |  | 398.9817
427.0782 |  | 427.0782
374.2437 |  | 374.2437
422.9151 |  | 422.9151
479.4087 |  | 479.4087
318.8997 |  | 318.8997
359.467 |  | 359.467
413.6934 |  | 413.6934
469.9181 |  | 469.9181
576.7129 |  | 576.7129
637.6666 |  | 637.6666
669.3599 |  | 669.3599
685.5374 |  | 685.5374
487.2856 |  | 487.2856
573.2974 |  | 573.2974
666.5942 |  | 666.5942
598.5182 |  | 598.5182
672.8213 |  | 672.8213
735.3325 |  | 735.3325
787.4175 |  | 787.4175
832.83 |  | 832.83
541.7729 |  | 541.7729
534.0678 |  | 534.0678
695.2568 |  | 695.2568
724.1837 |  | 724.1837
864.0628 |  | 864.0628
924.6022 |  | 924.6022
1036.8753 |  | 1036.8753
1098.4714 |  | 1098.4714
877.0156 |  | 877.0156
948.7162 |  | 948.7162
981.9574 |  | 981.9574
1058.92 |  | 1058.92
812.9455 |  | 812.9455
894.4426 |  | 894.4426
958.5264 |  | 958.5264
1092.3955 |  | 1092.3955
1108.1578 |  | 1108.1578
1179.7044 |  | 1179.7044
1257.8884 |  | 1257.8884
1397.6463 |  | 1397.6463
1556.5458 |  | 1556.5458
1658.4722 |  | 1658.4722
1749.9638 |  | 1749.9638
840.0118 |  | 840.0118
912.3919 |  | 912.3919
963.4895 |  | 963.4895
1003.339 |  | 1003.339
1234.2559 |  | 1234.2559
1338.3397 |  | 1338.3397
1409.7542 |  | 1409.7542
1493.981 |  | 1493.981
1550.69 |  | 1550.69
1352.693 |  | 1352.693
1398.703 |  | 1398.703
1508.9068 |  | 1508.9068
1674.3665 |  | 1674.3665
1200.4144 |  | 1200.4144
1283.8269 |  | 1283.8269
1416.7849 |  | 1416.7849
1508.8665 |  | 1508.8665
1598.8017 |  | 1598.8017
1689.4197 |  | 1689.4197
2092.9884 |  | 2092.9884
2346.9884 |  | 2346.9884
2529.5219 |  | 2529.5219
2703.7978 |  | 2703.7978
2169.9766 |  | 2169.9766
2284.2526 |  | 2284.2526
2385.0423 |  | 2385.0423
2493.7612 |  | 2493.7612
2617.6301 |  | 2617.6301
2227.2787 |  | 2227.2787
2407.488 |  | 2407.488
2508.3577 |  | 2508.3577
2624.9016 |  | 2624.9016
2111.5713 |  | 2111.5713
2305.4296 |  | 2305.4296
2491.2746 |  | 2491.2746
2766.6299 |  | 2766.6299
3069.239 |  | 3069.239
3426.3556 |  | 3426.3556
2867.819 |  | 2867.819
3379.8685 |  | 3379.8685
3737.7603 |  | 3737.7603
3875.064 |  | 3875.064
4004.1439 |  | 4004.1439
4295.2175 |  | 4295.2175
4595.0968 |  | 4595.0968
4656.6379 |  | 4656.6379
4664.6626 |  | 4664.6626
3448.9864 |  | 3448.9864
3639.5425 |  | 3639.5425
4042.4929 |  | 4042.4929
4332.4218 |  | 4332.4218
5072.7199 |  | 5072.7199
5521.0639 |  | 5521.0639
5727.2058 |  | 5727.2058
90.8476 |  | 181.6952
106.5592 |  | 213.1183
145.3387 |  | 290.6773
167.6172 |  | 335.2343
188.3547 |  | 376.7094
202.4879 |  | 404.9758
102.972 |  | 205.9439
116.1429 |  | 232.2859
133.8158 |  | 267.6317
150.196 |  | 300.3921
177.561 |  | 355.122
194.9972 |  | 389.9945
230.1371 |  | 460.2742
242.8034 |  | 485.6067
178.5455 |  | 357.091
208.9617 |  | 417.9234
260.8895 |  | 521.7789
297.3228 |  | 594.6456
273.669 |  | 547.3381
321.881 |  | 643.7619
360.1978 |  | 720.3955
376.0572 |  | 752.1143
261.6739 |  | 523.3477
299.9456 |  | 599.8912
365.149 |  | 730.298
403.7936 |  | 807.5873
402.7736 |  | 805.5473
183.5282 |  | 367.0563
235.9056 |  | 471.8113
254.5738 |  | 509.1476
278.649 |  | 557.2981
302.5651 |  | 605.1301
278.138 |  | 556.2759
343.952 |  | 687.904
398.9817 |  | 797.9634
427.0782 |  | 854.1563
374.2437 |  | 748.4875
422.9151 |  | 845.8302
479.4087 |  | 958.8173
318.8997 |  | 637.7994
359.467 |  | 718.934
413.6934 |  | 827.3869
469.9181 |  | 939.8361
576.7129 |  | 1153.4258
637.6666 |  | 1275.3332
669.3599 |  | 1338.7198
685.5374 |  | 1371.0747
487.2856 |  | 974.5712
573.2974 |  | 1146.5948
666.5942 |  | 1333.1883
598.5182 |  | 1197.0364
672.8213 |  | 1345.6425
735.3325 |  | 1470.665
787.4175 |  | 1574.835
832.83 |  | 1665.66
541.7729 |  | 1083.5457
534.0678 |  | 1068.1357
695.2568 |  | 1390.5137
724.1837 |  | 1448.3673
864.0628 |  | 1728.1255
924.6022 |  | 1849.2044
1036.8753 |  | 2073.7507
1098.4714 |  | 2196.9429
877.0156 |  | 1754.0312
948.7162 |  | 1897.4325
981.9574 |  | 1963.9148
1058.92 |  | 2117.8401
812.9455 |  | 1625.891
894.4426 |  | 1788.8851
958.5264 |  | 1917.0528
1092.3955 |  | 2184.791
1108.1578 |  | 2216.3155
1179.7044 |  | 2359.4087
1257.8884 |  | 2515.7767
1397.6463 |  | 2795.2926
1556.5458 |  | 3113.0916
1658.4722 |  | 3316.9444
1749.9638 |  | 3499.9275
840.0118 |  | 1680.0235
912.3919 |  | 1824.7838
963.4895 |  | 1926.979
1003.339 |  | 2006.678
1234.2559 |  | 2468.5118
1338.3397 |  | 2676.6794
1409.7542 |  | 2819.5084
1493.981 |  | 2987.9621
1550.69 |  | 3101.38
1352.693 |  | 2705.3861
1398.703 |  | 2797.406
1508.9068 |  | 3017.8135
1674.3665 |  | 3348.7331
1200.4144 |  | 2400.8289
1283.8269 |  | 2567.6538
1416.7849 |  | 2833.5698
1508.8665 |  | 3017.733
1598.8017 |  | 3197.6035
1689.4197 |  | 3378.8394
2092.9884 |  | 4185.9767
2346.9884 |  | 4693.9769
2529.5219 |  | 5059.0437
2703.7978 |  | 5407.5955
2169.9766 |  | 4339.9531
2284.2526 |  | 4568.5051
2385.0423 |  | 4770.0846
2493.7612 |  | 4987.5224
2617.6301 |  | 5235.2602
2227.2787 |  | 4454.5573
2407.488 |  | 4814.9761
2508.3577 |  | 5016.7154
2624.9016 |  | 5249.8033
2111.5713 |  | 4223.1426
2305.4296 |  | 4610.8591
2491.2746 |  | 4982.5492
2766.6299 |  | 5533.2599
3069.239 |  | 6138.4781
3426.3556 |  | 6852.7113
2867.819 |  | 5735.638
3379.8685 |  | 6759.737
3737.7603 |  | 7475.5206
3875.064 |  | 7750.128
4004.1439 |  | 8008.2879
4295.2175 |  | 8590.4351
4595.0968 |  | 9190.1937
4656.6379 |  | 9313.2758
4664.6626 |  | 9329.3252
3448.9864 |  | 6897.9727
3639.5425 |  | 7279.085
4042.4929 |  | 8084.9858
4332.4218 |  | 8664.8435
5072.7199 |  | 10145.4398
5521.0639 |  | 11042.1279
5727.2058 |  | 11454.4117
90.8476 |  | 272.5428
106.5592 |  | 319.6775
145.3387 |  | 436.016
167.6172 |  | 502.8515
188.3547 |  | 565.064
202.4879 |  | 607.4636
102.972 |  | 308.9159
116.1429 |  | 348.4288
133.8158 |  | 401.4475
150.196 |  | 450.5881
177.561 |  | 532.683
194.9972 |  | 584.9917
230.1371 |  | 690.4113
242.8034 |  | 728.4101
178.5455 |  | 535.6365
208.9617 |  | 626.885
260.8895 |  | 782.6684
297.3228 |  | 891.9684
273.669 |  | 821.0071
321.881 |  | 965.6429
360.1978 |  | 1080.5933
376.0572 |  | 1128.1715
261.6739 |  | 785.0216
299.9456 |  | 899.8369
365.149 |  | 1095.4471
403.7936 |  | 1211.3809
402.7736 |  | 1208.3209
183.5282 |  | 550.5845
235.9056 |  | 707.7169
254.5738 |  | 763.7214
278.649 |  | 835.9471
302.5651 |  | 907.6952
278.138 |  | 834.4139
343.952 |  | 1031.8561
398.9817 |  | 1196.9451
427.0782 |  | 1281.2345
374.2437 |  | 1122.7312
422.9151 |  | 1268.7454
479.4087 |  | 1438.226
318.8997 |  | 956.6991
359.467 |  | 1078.4011
413.6934 |  | 1241.0803
469.9181 |  | 1409.7542
576.7129 |  | 1730.1386
637.6666 |  | 1912.9998
669.3599 |  | 2008.0797
685.5374 |  | 2056.6121
487.2856 |  | 1461.8568
573.2974 |  | 1719.8922
666.5942 |  | 1999.7825
598.5182 |  | 1795.5546
672.8213 |  | 2018.4638
735.3325 |  | 2205.9974
787.4175 |  | 2362.2524
832.83 |  | 2498.4899
541.7729 |  | 1625.3186
534.0678 |  | 1602.2035
695.2568 |  | 2085.7705
724.1837 |  | 2172.551
864.0628 |  | 2592.1883
924.6022 |  | 2773.8066
1036.8753 |  | 3110.626
1098.4714 |  | 3295.4143
877.0156 |  | 2631.0468
948.7162 |  | 2846.1487
981.9574 |  | 2945.8722
1058.92 |  | 3176.7601
812.9455 |  | 2438.8364
894.4426 |  | 2683.3277
958.5264 |  | 2875.5792
1092.3955 |  | 3277.1865
1108.1578 |  | 3324.4733
1179.7044 |  | 3539.1131
1257.8884 |  | 3773.6651
1397.6463 |  | 4192.9389
1556.5458 |  | 4669.6374
1658.4722 |  | 4975.4165
1749.9638 |  | 5249.8913
840.0118 |  | 2520.0353
912.3919 |  | 2737.1757
963.4895 |  | 2890.4686
1003.339 |  | 3010.017
1234.2559 |  | 3702.7677
1338.3397 |  | 4015.019
1409.7542 |  | 4229.2626
1493.981 |  | 4481.9431
1550.69 |  | 4652.0699
1352.693 |  | 4058.0791
1398.703 |  | 4196.109
1508.9068 |  | 4526.7203
1674.3665 |  | 5023.0996
1200.4144 |  | 3601.2433
1283.8269 |  | 3851.4807
1416.7849 |  | 4250.3547
1508.8665 |  | 4526.5994
1598.8017 |  | 4796.4052
1689.4197 |  | 5068.259
2092.9884 |  | 6278.9651
2346.9884 |  | 7040.9653
2529.5219 |  | 7588.5656
2703.7978 |  | 8111.3933
2169.9766 |  | 6509.9297
2284.2526 |  | 6852.7577
2385.0423 |  | 7155.1269
2493.7612 |  | 7481.2836
2617.6301 |  | 7852.8904
2227.2787 |  | 6681.836
2407.488 |  | 7222.4641
2508.3577 |  | 7525.0732
2624.9016 |  | 7874.7049
2111.5713 |  | 6334.7139
2305.4296 |  | 6916.2887
2491.2746 |  | 7473.8238
2766.6299 |  | 8299.8898
3069.239 |  | 9207.7171
3426.3556 |  | 10279.0669
2867.819 |  | 8603.4569
3379.8685 |  | 10139.6056
3737.7603 |  | 11213.2809
3875.064 |  | 11625.1919
4004.1439 |  | 12012.4318
4295.2175 |  | 12885.6526
4595.0968 |  | 13785.2905
4656.6379 |  | 13969.9138
4664.6626 |  | 13993.9878
3448.9864 |  | 10346.9591
3639.5425 |  | 10918.6274
4042.4929 |  | 12127.4788
4332.4218 |  | 12997.2653
5072.7199 |  | 15218.1598
5521.0639 |  | 16563.1918
5727.2058 |  | 17181.6175
90.8476 |  | 363.3904
106.5592 |  | 426.2366
145.3387 |  | 581.3546
167.6172 |  | 670.4687
188.3547 |  | 753.4187
202.4879 |  | 809.9515
102.972 |  | 411.8879
116.1429 |  | 464.5717
133.8158 |  | 535.2633
150.196 |  | 600.7841
177.561 |  | 710.244
194.9972 |  | 779.989
230.1371 |  | 920.5484
242.8034 |  | 971.2134
178.5455 |  | 714.1819
208.9617 |  | 835.8467
260.8895 |  | 1043.5578
297.3228 |  | 1189.2912
273.669 |  | 1094.6762
321.881 |  | 1287.5239
360.1978 |  | 1440.7911
376.0572 |  | 1504.2286
261.6739 |  | 1046.6955
299.9456 |  | 1199.7825
365.149 |  | 1460.5961
403.7936 |  | 1615.1746
402.7736 |  | 1611.0945
183.5282 |  | 734.1127
235.9056 |  | 943.6226
254.5738 |  | 1018.2952
278.649 |  | 1114.5962
302.5651 |  | 1210.2603
278.138 |  | 1112.5518
343.952 |  | 1375.8081
398.9817 |  | 1595.9268
427.0782 |  | 1708.3126
374.2437 |  | 1496.975
422.9151 |  | 1691.6605
479.4087 |  | 1917.6347
318.8997 |  | 1275.5988
359.467 |  | 1437.8681
413.6934 |  | 1654.7738
469.9181 |  | 1879.6723
576.7129 |  | 2306.8515
637.6666 |  | 2550.6665
669.3599 |  | 2677.4396
685.5374 |  | 2742.1495
487.2856 |  | 1949.1425
573.2974 |  | 2293.1896
666.5942 |  | 2666.3766
598.5182 |  | 2394.0728
672.8213 |  | 2691.2851
735.3325 |  | 2941.3299
787.4175 |  | 3149.6699
832.83 |  | 3331.3199
541.7729 |  | 2167.0915
534.0678 |  | 2136.2714
695.2568 |  | 2781.0273
724.1837 |  | 2896.7347
864.0628 |  | 3456.2511
924.6022 |  | 3698.4088
1036.8753 |  | 4147.5013
1098.4714 |  | 4393.8858
877.0156 |  | 3508.0625
948.7162 |  | 3794.8649
981.9574 |  | 3927.8296
1058.92 |  | 4235.6802
812.9455 |  | 3251.7819
894.4426 |  | 3577.7702
958.5264 |  | 3834.1056
1092.3955 |  | 4369.582
1108.1578 |  | 4432.631
1179.7044 |  | 4718.8174
1257.8884 |  | 5031.5535
1397.6463 |  | 5590.5852
1556.5458 |  | 6226.1832
1658.4722 |  | 6633.8887
1749.9638 |  | 6999.8551
840.0118 |  | 3360.047
912.3919 |  | 3649.5676
963.4895 |  | 3853.9581
1003.339 |  | 4013.356
1234.2559 |  | 4937.0235
1338.3397 |  | 5353.3587
1409.7542 |  | 5639.0168
1493.981 |  | 5975.9242
1550.69 |  | 6202.7599
1352.693 |  | 5410.7721
1398.703 |  | 5594.812
1508.9068 |  | 6035.6271
1674.3665 |  | 6697.4661
1200.4144 |  | 4801.6577
1283.8269 |  | 5135.3076
1416.7849 |  | 5667.1396
1508.8665 |  | 6035.4659
1598.8017 |  | 6395.207
1689.4197 |  | 6757.6787
2092.9884 |  | 8371.9535
2346.9884 |  | 9387.9538
2529.5219 |  | 10118.0875
2703.7978 |  | 10815.191
2169.9766 |  | 8679.9063
2284.2526 |  | 9137.0102
2385.0423 |  | 9540.1692
2493.7612 |  | 9975.0448
2617.6301 |  | 10470.5205
2227.2787 |  | 8909.1146
2407.488 |  | 9629.9521
2508.3577 |  | 10033.4309
2624.9016 |  | 10499.6065
2111.5713 |  | 8446.2852
2305.4296 |  | 9221.7182
2491.2746 |  | 9965.0984
2766.6299 |  | 11066.5198
3069.239 |  | 12276.9561
3426.3556 |  | 13705.4225
2867.819 |  | 11471.2759
3379.8685 |  | 13519.4741
3737.7603 |  | 14951.0411
3875.064 |  | 15500.2559
4004.1439 |  | 16016.5758
4295.2175 |  | 17180.8701
4595.0968 |  | 18380.3874
4656.6379 |  | 18626.5517
4664.6626 |  | 18658.6504
3448.9864 |  | 13795.9455
3639.5425 |  | 14558.1699
4042.4929 |  | 16169.9717
4332.4218 |  | 17329.687
5072.7199 |  | 20290.8797
5521.0639 |  | 22084.2557
5727.2058 |  | 22908.8234

## Max flow to diameter_Completed
Max Branch Flow (gpm) | Max Branch Diameter (in.) | Max Header Flow (gpm) | Max Header Diameter (in.)
90.8476 | 2.5 | 181.6952 | 3
106.5592 | 2.5 | 213.1183 | 3
145.3387 | 3 | 290.6773 | 4
167.6172 | 3 | 335.2343 | 4
188.3547 | 3 | 376.7094 | 4
202.4879 | 3 | 404.9758 | 5
102.972 | 2.5 | 205.9439 | 3
116.1429 | 2.5 | 232.2859 | 4
133.8158 | 3 | 267.6317 | 4
150.196 | 3 | 300.3921 | 4
177.561 | 3 | 355.122 | 4
194.9972 | 3 | 389.9945 | 4
230.1371 | 4 | 460.2742 | 5
242.8034 | 4 | 485.6067 | 5
178.5455 | 3 | 357.091 | 4
208.9617 | 3 | 417.9234 | 5
260.8895 | 4 | 521.7789 | 5
297.3228 | 4 | 594.6456 | 5
273.669 | 4 | 547.3381 | 5
321.881 | 4 | 643.7619 | 5
360.1978 | 4 | 720.3955 | 6
376.0572 | 4 | 752.1143 | 6
261.6739 | 4 | 523.3477 | 5
299.9456 | 4 | 599.8912 | 5
365.149 | 4 | 730.298 | 6
403.7936 | 5 | 807.5873 | 6
402.7736 | 5 | 805.5473 | 6
183.5282 | 3 | 367.0563 | 4
235.9056 | 4 | 471.8113 | 5
254.5738 | 4 | 509.1476 | 5
278.649 | 4 | 557.2981 | 5
302.5651 | 4 | 605.1301 | 5
278.138 | 4 | 556.2759 | 5
343.952 | 4 | 687.904 | 6
398.9817 | 4 | 797.9634 | 6
427.0782 | 5 | 854.1563 | 6
374.2437 | 4 | 748.4875 | 6
422.9151 | 5 | 845.8302 | 6
479.4087 | 5 | 958.8173 | 8
318.8997 | 4 | 637.7994 | 5
359.467 | 4 | 718.934 | 6
413.6934 | 5 | 827.3869 | 6
469.9181 | 5 | 939.8361 | 6
576.7129 | 5 | 1153.4258 | 8
637.6666 | 5 | 1275.3332 | 8
669.3599 | 6 | 1338.7198 | 8
685.5374 | 6 | 1371.0747 | 8
487.2856 | 5 | 974.5712 | 8
573.2974 | 5 | 1146.5948 | 8
666.5942 | 6 | 1333.1883 | 8
598.5182 | 5 | 1197.0364 | 8
672.8213 | 6 | 1345.6425 | 8
735.3325 | 6 | 1470.665 | 8
787.4175 | 6 | 1574.835 | 8
832.83 | 6 | 1665.66 | 10
541.7729 | 5 | 1083.5457 | 8
534.0678 | 5 | 1068.1357 | 8
695.2568 | 6 | 1390.5137 | 8
724.1837 | 6 | 1448.3673 | 8
864.0628 | 6 | 1728.1255 | 10
924.6022 | 6 | 1849.2044 | 10
1036.8753 | 8 | 2073.7507 | 10
1098.4714 | 8 | 2196.9429 | 10
877.0156 | 6 | 1754.0312 | 10
948.7162 | 6 | 1897.4325 | 10
981.9574 | 8 | 1963.9148 | 10
1058.92 | 8 | 2117.8401 | 10
812.9455 | 6 | 1625.891 | 10
894.4426 | 6 | 1788.8851 | 10
958.5264 | 8 | 1917.0528 | 10
1092.3955 | 8 | 2184.791 | 10
1108.1578 | 8 | 2216.3155 | 10
1179.7044 | 8 | 2359.4087 | 10
1257.8884 | 8 | 2515.7767 | 12
1397.6463 | 8 | 2795.2926 | 12
1556.5458 | 8 | 3113.0916 | 12
1658.4722 | 10 | 3316.9444 | 12
1749.9638 | 10 | 3499.9275 | 12
840.0118 | 6 | 1680.0235 | 10
912.3919 | 6 | 1824.7838 | 10
963.4895 | 8 | 1926.979 | 10
1003.339 | 8 | 2006.678 | 10
1234.2559 | 8 | 2468.5118 | 10
1338.3397 | 8 | 2676.6794 | 12
1409.7542 | 8 | 2819.5084 | 12
1493.981 | 8 | 2987.9621 | 12
1550.69 | 8 | 3101.38 | 12
1352.693 | 8 | 2705.3861 | 12
1398.703 | 8 | 2797.406 | 12
1508.9068 | 8 | 3017.8135 | 12
1674.3665 | 10 | 3348.7331 | 12
1200.4144 | 8 | 2400.8289 | 10
1283.8269 | 8 | 2567.6538 | 12
1416.7849 | 8 | 2833.5698 | 12
1508.8665 | 8 | 3017.733 | 12
1598.8017 | 8 | 3197.6035 | 12
1689.4197 | 10 | 3378.8394 | 12
2092.9884 | 10 | 4185.9767 | 14
2346.9884 | 10 | 4693.9769 | 16
2529.5219 | 12 | 5059.0437 | 16
2703.7978 | 12 | 5407.5955 | 16
2169.9766 | 10 | 4339.9531 | 16
2284.2526 | 10 | 4568.5051 | 16
2385.0423 | 10 | 4770.0846 | 16
2493.7612 | 10 | 4987.5224 | 16
2617.6301 | 12 | 5235.2602 | 16
2227.2787 | 10 | 4454.5573 | 16
2407.488 | 10 | 4814.9761 | 16
2508.3577 | 12 | 5016.7154 | 16
2624.9016 | 12 | 5249.8033 | 16
2111.5713 | 10 | 4223.1426 | 14
2305.4296 | 10 | 4610.8591 | 16
2491.2746 | 10 | 4982.5492 | 16
2766.6299 | 12 | 5533.2599 | 16
3069.239 | 12 | 6138.4781 | 18
3426.3556 | 12 | 6852.7113 | 18
2867.819 | 12 | 5735.638 | 18
3379.8685 | 12 | 6759.737 | 18
3737.7603 | 14 | 7475.5206 | 20
3875.064 | 14 | 7750.128 | 20
4004.1439 | 14 | 8008.2879 | 20
4295.2175 | 16 | 8590.4351 | 20
4595.0968 | 16 | 9190.1937 | 24
4656.6379 | 16 | 9313.2758 | 24
4664.6626 | 16 | 9329.3252 | 24
3448.9864 | 12 | 6897.9727 | 18
3639.5425 | 14 | 7279.085 | 20
4042.4929 | 14 | 8084.9858 | 20
4332.4218 | 16 | 8664.8435 | 20
5072.7199 | 16 | 10145.4398 | 24
5521.0639 | 16 | 11042.1279 | 24
5727.2058 | 18 | 11454.4117 | 24
90.8476 | 2.5 | 272.5428 | 4
106.5592 | 2.5 | 319.6775 | 4
145.3387 | 3 | 436.016 | 5
167.6172 | 3 | 502.8515 | 5
188.3547 | 3 | 565.064 | 5
202.4879 | 3 | 607.4636 | 5
102.972 | 2.5 | 308.9159 | 4
116.1429 | 2.5 | 348.4288 | 4
133.8158 | 3 | 401.4475 | 5
150.196 | 3 | 450.5881 | 5
177.561 | 3 | 532.683 | 5
194.9972 | 3 | 584.9917 | 5
230.1371 | 4 | 690.4113 | 6
242.8034 | 4 | 728.4101 | 6
178.5455 | 3 | 535.6365 | 5
208.9617 | 3 | 626.885 | 5
260.8895 | 4 | 782.6684 | 6
297.3228 | 4 | 891.9684 | 6
273.669 | 4 | 821.0071 | 6
321.881 | 4 | 965.6429 | 8
360.1978 | 4 | 1080.5933 | 8
376.0572 | 4 | 1128.1715 | 8
261.6739 | 4 | 785.0216 | 6
299.9456 | 4 | 899.8369 | 6
365.149 | 4 | 1095.4471 | 8
403.7936 | 5 | 1211.3809 | 8
402.7736 | 5 | 1208.3209 | 8
183.5282 | 3 | 550.5845 | 5
235.9056 | 4 | 707.7169 | 6
254.5738 | 4 | 763.7214 | 6
278.649 | 4 | 835.9471 | 6
302.5651 | 4 | 907.6952 | 6
278.138 | 4 | 834.4139 | 6
343.952 | 4 | 1031.8561 | 8
398.9817 | 4 | 1196.9451 | 8
427.0782 | 5 | 1281.2345 | 8
374.2437 | 4 | 1122.7312 | 8
422.9151 | 5 | 1268.7454 | 8
479.4087 | 5 | 1438.226 | 8
318.8997 | 4 | 956.6991 | 8
359.467 | 4 | 1078.4011 | 8
413.6934 | 5 | 1241.0803 | 8
469.9181 | 5 | 1409.7542 | 8
576.7129 | 5 | 1730.1386 | 10
637.6666 | 5 | 1912.9998 | 10
669.3599 | 6 | 2008.0797 | 10
685.5374 | 6 | 2056.6121 | 10
487.2856 | 5 | 1461.8568 | 8
573.2974 | 5 | 1719.8922 | 10
666.5942 | 6 | 1999.7825 | 10
598.5182 | 5 | 1795.5546 | 10
672.8213 | 6 | 2018.4638 | 10
735.3325 | 6 | 2205.9974 | 10
787.4175 | 6 | 2362.2524 | 10
832.83 | 6 | 2498.4899 | 10
541.7729 | 5 | 1625.3186 | 10
534.0678 | 5 | 1602.2035 | 10
695.2568 | 6 | 2085.7705 | 10
724.1837 | 6 | 2172.551 | 10
864.0628 | 6 | 2592.1883 | 12
924.6022 | 6 | 2773.8066 | 12
1036.8753 | 8 | 3110.626 | 12
1098.4714 | 8 | 3295.4143 | 12
877.0156 | 6 | 2631.0468 | 12
948.7162 | 6 | 2846.1487 | 12
981.9574 | 8 | 2945.8722 | 12
1058.92 | 8 | 3176.7601 | 12
812.9455 | 6 | 2438.8364 | 10
894.4426 | 6 | 2683.3277 | 12
958.5264 | 8 | 2875.5792 | 12
1092.3955 | 8 | 3277.1865 | 12
1108.1578 | 8 | 3324.4733 | 12
1179.7044 | 8 | 3539.1131 | 12
1257.8884 | 8 | 3773.6651 | 14
1397.6463 | 8 | 4192.9389 | 14
1556.5458 | 8 | 4669.6374 | 16
1658.4722 | 10 | 4975.4165 | 16
1749.9638 | 10 | 5249.8913 | 16
840.0118 | 6 | 2520.0353 | 12
912.3919 | 6 | 2737.1757 | 12
963.4895 | 8 | 2890.4686 | 12
1003.339 | 8 | 3010.017 | 12
1234.2559 | 8 | 3702.7677 | 14
1338.3397 | 8 | 4015.019 | 14
1409.7542 | 8 | 4229.2626 | 14
1493.981 | 8 | 4481.9431 | 16
1550.69 | 8 | 4652.0699 | 16
1352.693 | 8 | 4058.0791 | 14
1398.703 | 8 | 4196.109 | 14
1508.9068 | 8 | 4526.7203 | 16
1674.3665 | 10 | 5023.0996 | 16
1200.4144 | 8 | 3601.2433 | 14
1283.8269 | 8 | 3851.4807 | 14
1416.7849 | 8 | 4250.3547 | 16
1508.8665 | 8 | 4526.5994 | 16
1598.8017 | 8 | 4796.4052 | 16
1689.4197 | 10 | 5068.259 | 16
2092.9884 | 10 | 6278.9651 | 18
2346.9884 | 10 | 7040.9653 | 18
2529.5219 | 12 | 7588.5656 | 20
2703.7978 | 12 | 8111.3933 | 20
2169.9766 | 10 | 6509.9297 | 18
2284.2526 | 10 | 6852.7577 | 18
2385.0423 | 10 | 7155.1269 | 20
2493.7612 | 10 | 7481.2836 | 20
2617.6301 | 12 | 7852.8904 | 20
2227.2787 | 10 | 6681.836 | 18
2407.488 | 10 | 7222.4641 | 20
2508.3577 | 12 | 7525.0732 | 20
2624.9016 | 12 | 7874.7049 | 20
2111.5713 | 10 | 6334.7139 | 18
2305.4296 | 10 | 6916.2887 | 18
2491.2746 | 10 | 7473.8238 | 20
2766.6299 | 12 | 8299.8898 | 20
3069.239 | 12 | 9207.7171 | 24
3426.3556 | 12 | 10279.0669 | 24
2867.819 | 12 | 8603.4569 | 20
3379.8685 | 12 | 10139.6056 | 24
3737.7603 | 14 | 11213.2809 | 24
3875.064 | 14 | 11625.1919 | 24
4004.1439 | 14 | 12012.4318 | 24
4295.2175 | 16 | 12885.6526 | 24
4595.0968 | 16 | 13785.2905 | 24
4656.6379 | 16 | 13969.9138 | 24
4664.6626 | 16 | 13993.9878 | 24
3448.9864 | 12 | 10346.9591 | 24
3639.5425 | 14 | 10918.6274 | 24
4042.4929 | 14 | 12127.4788 | 24
4332.4218 | 16 | 12997.2653 | 24
5072.7199 | 16 | 15218.1598 | 24
5521.0639 | 16 | 16563.1918 | 24
5727.2058 | 18 | 17181.6175 | 24
90.8476 | 2.5 | 363.3904 | 4
106.5592 | 2.5 | 426.2366 | 5
145.3387 | 3 | 581.3546 | 5
167.6172 | 3 | 670.4687 | 6
188.3547 | 3 | 753.4187 | 6
202.4879 | 3 | 809.9515 | 6
102.972 | 2.5 | 411.8879 | 5
116.1429 | 2.5 | 464.5717 | 5
133.8158 | 3 | 535.2633 | 5
150.196 | 3 | 600.7841 | 5
177.561 | 3 | 710.244 | 6
194.9972 | 3 | 779.989 | 6
230.1371 | 4 | 920.5484 | 6
242.8034 | 4 | 971.2134 | 8
178.5455 | 3 | 714.1819 | 6
208.9617 | 3 | 835.8467 | 6
260.8895 | 4 | 1043.5578 | 8
297.3228 | 4 | 1189.2912 | 8
273.669 | 4 | 1094.6762 | 8
321.881 | 4 | 1287.5239 | 8
360.1978 | 4 | 1440.7911 | 8
376.0572 | 4 | 1504.2286 | 8
261.6739 | 4 | 1046.6955 | 8
299.9456 | 4 | 1199.7825 | 8
365.149 | 4 | 1460.5961 | 8
403.7936 | 5 | 1615.1746 | 10
402.7736 | 5 | 1611.0945 | 10
183.5282 | 3 | 734.1127 | 6
235.9056 | 4 | 943.6226 | 6
254.5738 | 4 | 1018.2952 | 8
278.649 | 4 | 1114.5962 | 8
302.5651 | 4 | 1210.2603 | 8
278.138 | 4 | 1112.5518 | 8
343.952 | 4 | 1375.8081 | 8
398.9817 | 4 | 1595.9268 | 8
427.0782 | 5 | 1708.3126 | 10
374.2437 | 4 | 1496.975 | 8
422.9151 | 5 | 1691.6605 | 10
479.4087 | 5 | 1917.6347 | 10
318.8997 | 4 | 1275.5988 | 8
359.467 | 4 | 1437.8681 | 8
413.6934 | 5 | 1654.7738 | 10
469.9181 | 5 | 1879.6723 | 10
576.7129 | 5 | 2306.8515 | 10
637.6666 | 5 | 2550.6665 | 12
669.3599 | 6 | 2677.4396 | 12
685.5374 | 6 | 2742.1495 | 12
487.2856 | 5 | 1949.1425 | 10
573.2974 | 5 | 2293.1896 | 10
666.5942 | 6 | 2666.3766 | 12
598.5182 | 5 | 2394.0728 | 10
672.8213 | 6 | 2691.2851 | 12
735.3325 | 6 | 2941.3299 | 12
787.4175 | 6 | 3149.6699 | 12
832.83 | 6 | 3331.3199 | 12
541.7729 | 5 | 2167.0915 | 10
534.0678 | 5 | 2136.2714 | 10
695.2568 | 6 | 2781.0273 | 12
724.1837 | 6 | 2896.7347 | 12
864.0628 | 6 | 3456.2511 | 12
924.6022 | 6 | 3698.4088 | 14
1036.8753 | 8 | 4147.5013 | 14
1098.4714 | 8 | 4393.8858 | 16
877.0156 | 6 | 3508.0625 | 12
948.7162 | 6 | 3794.8649 | 14
981.9574 | 8 | 3927.8296 | 14
1058.92 | 8 | 4235.6802 | 14
812.9455 | 6 | 3251.7819 | 12
894.4426 | 6 | 3577.7702 | 14
958.5264 | 8 | 3834.1056 | 14
1092.3955 | 8 | 4369.582 | 16
1108.1578 | 8 | 4432.631 | 16
1179.7044 | 8 | 4718.8174 | 16
1257.8884 | 8 | 5031.5535 | 16
1397.6463 | 8 | 5590.5852 | 18
1556.5458 | 8 | 6226.1832 | 18
1658.4722 | 10 | 6633.8887 | 18
1749.9638 | 10 | 6999.8551 | 18
840.0118 | 6 | 3360.047 | 12
912.3919 | 6 | 3649.5676 | 14
963.4895 | 8 | 3853.9581 | 14
1003.339 | 8 | 4013.356 | 14
1234.2559 | 8 | 4937.0235 | 16
1338.3397 | 8 | 5353.3587 | 16
1409.7542 | 8 | 5639.0168 | 18
1493.981 | 8 | 5975.9242 | 18
1550.69 | 8 | 6202.7599 | 18
1352.693 | 8 | 5410.7721 | 16
1398.703 | 8 | 5594.812 | 18
1508.9068 | 8 | 6035.6271 | 18
1674.3665 | 10 | 6697.4661 | 18
1200.4144 | 8 | 4801.6577 | 16
1283.8269 | 8 | 5135.3076 | 16
1416.7849 | 8 | 5667.1396 | 18
1508.8665 | 8 | 6035.4659 | 18
1598.8017 | 8 | 6395.207 | 18
1689.4197 | 10 | 6757.6787 | 18
2092.9884 | 10 | 8371.9535 | 20
2346.9884 | 10 | 9387.9538 | 24
2529.5219 | 12 | 10118.0875 | 24
2703.7978 | 12 | 10815.191 | 24
2169.9766 | 10 | 8679.9063 | 20
2284.2526 | 10 | 9137.0102 | 24
2385.0423 | 10 | 9540.1692 | 24
2493.7612 | 10 | 9975.0448 | 24
2617.6301 | 12 | 10470.5205 | 24
2227.2787 | 10 | 8909.1146 | 24
2407.488 | 10 | 9629.9521 | 24
2508.3577 | 12 | 10033.4309 | 24
2624.9016 | 12 | 10499.6065 | 24
2111.5713 | 10 | 8446.2852 | 20
2305.4296 | 10 | 9221.7182 | 24
2491.2746 | 10 | 9965.0984 | 24
2766.6299 | 12 | 11066.5198 | 24
3069.239 | 12 | 12276.9561 | 24
3426.3556 | 12 | 13705.4225 | 24
2867.819 | 12 | 11471.2759 | 24
3379.8685 | 12 | 13519.4741 | 24
3737.7603 | 14 | 14951.0411 | 24
3875.064 | 14 | 15500.2559 | 24
4004.1439 | 14 | 16016.5758 | 24
4295.2175 | 16 | 17180.8701 | 24
4595.0968 | 16 | 18380.3874 | 24
4656.6379 | 16 | 18626.5517 | 24
4664.6626 | 16 | 18658.6504 | 24
3448.9864 | 12 | 13795.9455 | 24
3639.5425 | 14 | 14558.1699 | 24
4042.4929 | 14 | 16169.9717 | 24
4332.4218 | 16 | 17329.687 | 24
5072.7199 | 16 | 20290.8797 | 24
5521.0639 | 16 | 22084.2557 | 24
5727.2058 | 18 | 22908.8234 | 24
90.8476 | 2.5 | 90.8476 | 2.5
106.5592 | 2.5 | 106.5592 | 2.5
145.3387 | 3 | 145.3387 | 3
167.6172 | 3 | 167.6172 | 3
188.3547 | 3 | 188.3547 | 3
202.4879 | 3 | 202.4879 | 3
102.972 | 2.5 | 102.972 | 2.5
116.1429 | 2.5 | 116.1429 | 2.5
133.8158 | 3 | 133.8158 | 3
150.196 | 3 | 150.196 | 3
177.561 | 3 | 177.561 | 3
194.9972 | 3 | 194.9972 | 3
230.1371 | 4 | 230.1371 | 4
242.8034 | 4 | 242.8034 | 4
178.5455 | 3 | 178.5455 | 3
208.9617 | 3 | 208.9617 | 3
260.8895 | 4 | 260.8895 | 4
297.3228 | 4 | 297.3228 | 4
273.669 | 4 | 273.669 | 4
321.881 | 4 | 321.881 | 4
360.1978 | 4 | 360.1978 | 4
376.0572 | 4 | 376.0572 | 4
261.6739 | 4 | 261.6739 | 4
299.9456 | 4 | 299.9456 | 4
365.149 | 4 | 365.149 | 4
403.7936 | 5 | 403.7936 | 5
402.7736 | 5 | 402.7736 | 5
183.5282 | 3 | 183.5282 | 3
235.9056 | 4 | 235.9056 | 4
254.5738 | 4 | 254.5738 | 4
278.649 | 4 | 278.649 | 4
302.5651 | 4 | 302.5651 | 4
278.138 | 4 | 278.138 | 4
343.952 | 4 | 343.952 | 4
398.9817 | 4 | 398.9817 | 4
427.0782 | 5 | 427.0782 | 5
374.2437 | 4 | 374.2437 | 4
422.9151 | 5 | 422.9151 | 5
479.4087 | 5 | 479.4087 | 5
318.8997 | 4 | 318.8997 | 4
359.467 | 4 | 359.467 | 4
413.6934 | 5 | 413.6934 | 5
469.9181 | 5 | 469.9181 | 5
576.7129 | 5 | 576.7129 | 5
637.6666 | 5 | 637.6666 | 5
669.3599 | 6 | 669.3599 | 6
685.5374 | 6 | 685.5374 | 6
487.2856 | 5 | 487.2856 | 5
573.2974 | 5 | 573.2974 | 5
666.5942 | 6 | 666.5942 | 6
598.5182 | 5 | 598.5182 | 5
672.8213 | 6 | 672.8213 | 6
735.3325 | 6 | 735.3325 | 6
787.4175 | 6 | 787.4175 | 6
832.83 | 6 | 832.83 | 6
541.7729 | 5 | 541.7729 | 5
534.0678 | 5 | 534.0678 | 5
695.2568 | 6 | 695.2568 | 6
724.1837 | 6 | 724.1837 | 6
864.0628 | 6 | 864.0628 | 6
924.6022 | 6 | 924.6022 | 6
1036.8753 | 8 | 1036.8753 | 8
1098.4714 | 8 | 1098.4714 | 8
877.0156 | 6 | 877.0156 | 6
948.7162 | 6 | 948.7162 | 6
981.9574 | 8 | 981.9574 | 8
1058.92 | 8 | 1058.92 | 8
812.9455 | 6 | 812.9455 | 6
894.4426 | 6 | 894.4426 | 6
958.5264 | 8 | 958.5264 | 8
1092.3955 | 8 | 1092.3955 | 8
1108.1578 | 8 | 1108.1578 | 8
1179.7044 | 8 | 1179.7044 | 8
1257.8884 | 8 | 1257.8884 | 8
1397.6463 | 8 | 1397.6463 | 8
1556.5458 | 8 | 1556.5458 | 8
1658.4722 | 10 | 1658.4722 | 10
1749.9638 | 10 | 1749.9638 | 10
840.0118 | 6 | 840.0118 | 6
912.3919 | 6 | 912.3919 | 6
963.4895 | 8 | 963.4895 | 8
1003.339 | 8 | 1003.339 | 8
1234.2559 | 8 | 1234.2559 | 8
1338.3397 | 8 | 1338.3397 | 8
1409.7542 | 8 | 1409.7542 | 8
1493.981 | 8 | 1493.981 | 8
1550.69 | 8 | 1550.69 | 8
1352.693 | 8 | 1352.693 | 8
1398.703 | 8 | 1398.703 | 8
1508.9068 | 8 | 1508.9068 | 8
1674.3665 | 10 | 1674.3665 | 10
1200.4144 | 8 | 1200.4144 | 8
1283.8269 | 8 | 1283.8269 | 8
1416.7849 | 8 | 1416.7849 | 8
1508.8665 | 8 | 1508.8665 | 8
1598.8017 | 8 | 1598.8017 | 8
1689.4197 | 10 | 1689.4197 | 10
2092.9884 | 10 | 2092.9884 | 10
2346.9884 | 10 | 2346.9884 | 10
2529.5219 | 12 | 2529.5219 | 12
2703.7978 | 12 | 2703.7978 | 12
2169.9766 | 10 | 2169.9766 | 10
2284.2526 | 10 | 2284.2526 | 10
2385.0423 | 10 | 2385.0423 | 10
2493.7612 | 10 | 2493.7612 | 10
2617.6301 | 12 | 2617.6301 | 12
2227.2787 | 10 | 2227.2787 | 10
2407.488 | 10 | 2407.488 | 10
2508.3577 | 12 | 2508.3577 | 12
2624.9016 | 12 | 2624.9016 | 12
2111.5713 | 10 | 2111.5713 | 10
2305.4296 | 10 | 2305.4296 | 10
2491.2746 | 10 | 2491.2746 | 10
2766.6299 | 12 | 2766.6299 | 12
3069.239 | 12 | 3069.239 | 12
3426.3556 | 12 | 3426.3556 | 12
2867.819 | 12 | 2867.819 | 12
3379.8685 | 12 | 3379.8685 | 12
3737.7603 | 14 | 3737.7603 | 14
3875.064 | 14 | 3875.064 | 14
4004.1439 | 14 | 4004.1439 | 14
4295.2175 | 16 | 4295.2175 | 16
4595.0968 | 16 | 4595.0968 | 16
4656.6379 | 16 | 4656.6379 | 16
4664.6626 | 16 | 4664.6626 | 16
3448.9864 | 12 | 3448.9864 | 12
3639.5425 | 14 | 3639.5425 | 14
4042.4929 | 14 | 4042.4929 | 14
4332.4218 | 16 | 4332.4218 | 16
5072.7199 | 16 | 5072.7199 | 16
5521.0639 | 16 | 5521.0639 | 16
5727.2058 | 18 | 5727.2058 | 18
90.8476 | 2.5 | 181.6952 | 3
106.5592 | 2.5 | 213.1183 | 3
145.3387 | 3 | 290.6773 | 4
167.6172 | 3 | 335.2343 | 4
188.3547 | 3 | 376.7094 | 4
202.4879 | 3 | 404.9758 | 5
102.972 | 2.5 | 205.9439 | 3
116.1429 | 2.5 | 232.2859 | 4
133.8158 | 3 | 267.6317 | 4
150.196 | 3 | 300.3921 | 4
177.561 | 3 | 355.122 | 4
194.9972 | 3 | 389.9945 | 4
230.1371 | 4 | 460.2742 | 5
242.8034 | 4 | 485.6067 | 5
178.5455 | 3 | 357.091 | 4
208.9617 | 3 | 417.9234 | 5
260.8895 | 4 | 521.7789 | 5
297.3228 | 4 | 594.6456 | 5
273.669 | 4 | 547.3381 | 5
321.881 | 4 | 643.7619 | 5
360.1978 | 4 | 720.3955 | 6
376.0572 | 4 | 752.1143 | 6
261.6739 | 4 | 523.3477 | 5
299.9456 | 4 | 599.8912 | 5
365.149 | 4 | 730.298 | 6
403.7936 | 5 | 807.5873 | 6
402.7736 | 5 | 805.5473 | 6
183.5282 | 3 | 367.0563 | 4
235.9056 | 4 | 471.8113 | 5
254.5738 | 4 | 509.1476 | 5
278.649 | 4 | 557.2981 | 5
302.5651 | 4 | 605.1301 | 5
278.138 | 4 | 556.2759 | 5
343.952 | 4 | 687.904 | 6
398.9817 | 4 | 797.9634 | 6
427.0782 | 5 | 854.1563 | 6
374.2437 | 4 | 748.4875 | 6
422.9151 | 5 | 845.8302 | 6
479.4087 | 5 | 958.8173 | 8
318.8997 | 4 | 637.7994 | 5
359.467 | 4 | 718.934 | 6
413.6934 | 5 | 827.3869 | 6
469.9181 | 5 | 939.8361 | 6
576.7129 | 5 | 1153.4258 | 8
637.6666 | 5 | 1275.3332 | 8
669.3599 | 6 | 1338.7198 | 8
685.5374 | 6 | 1371.0747 | 8
487.2856 | 5 | 974.5712 | 8
573.2974 | 5 | 1146.5948 | 8
666.5942 | 6 | 1333.1883 | 8
598.5182 | 5 | 1197.0364 | 8
672.8213 | 6 | 1345.6425 | 8
735.3325 | 6 | 1470.665 | 8
787.4175 | 6 | 1574.835 | 8
832.83 | 6 | 1665.66 | 10
541.7729 | 5 | 1083.5457 | 8
534.0678 | 5 | 1068.1357 | 8
695.2568 | 6 | 1390.5137 | 8
724.1837 | 6 | 1448.3673 | 8
864.0628 | 6 | 1728.1255 | 10
924.6022 | 6 | 1849.2044 | 10
1036.8753 | 8 | 2073.7507 | 10
1098.4714 | 8 | 2196.9429 | 10
877.0156 | 6 | 1754.0312 | 10
948.7162 | 6 | 1897.4325 | 10
981.9574 | 8 | 1963.9148 | 10
1058.92 | 8 | 2117.8401 | 10
812.9455 | 6 | 1625.891 | 10
894.4426 | 6 | 1788.8851 | 10
958.5264 | 8 | 1917.0528 | 10
1092.3955 | 8 | 2184.791 | 10
1108.1578 | 8 | 2216.3155 | 10
1179.7044 | 8 | 2359.4087 | 10
1257.8884 | 8 | 2515.7767 | 12
1397.6463 | 8 | 2795.2926 | 12
1556.5458 | 8 | 3113.0916 | 12
1658.4722 | 10 | 3316.9444 | 12
1749.9638 | 10 | 3499.9275 | 12
840.0118 | 6 | 1680.0235 | 10
912.3919 | 6 | 1824.7838 | 10
963.4895 | 8 | 1926.979 | 10
1003.339 | 8 | 2006.678 | 10
1234.2559 | 8 | 2468.5118 | 10
1338.3397 | 8 | 2676.6794 | 12
1409.7542 | 8 | 2819.5084 | 12
1493.981 | 8 | 2987.9621 | 12
1550.69 | 8 | 3101.38 | 12
1352.693 | 8 | 2705.3861 | 12
1398.703 | 8 | 2797.406 | 12
1508.9068 | 8 | 3017.8135 | 12
1674.3665 | 10 | 3348.7331 | 12
1200.4144 | 8 | 2400.8289 | 10
1283.8269 | 8 | 2567.6538 | 12
1416.7849 | 8 | 2833.5698 | 12
1508.8665 | 8 | 3017.733 | 12
1598.8017 | 8 | 3197.6035 | 12
1689.4197 | 10 | 3378.8394 | 12
2092.9884 | 10 | 4185.9767 | 14
2346.9884 | 10 | 4693.9769 | 16
2529.5219 | 12 | 5059.0437 | 16
2703.7978 | 12 | 5407.5955 | 16
2169.9766 | 10 | 4339.9531 | 16
2284.2526 | 10 | 4568.5051 | 16
2385.0423 | 10 | 4770.0846 | 16
2493.7612 | 10 | 4987.5224 | 16
2617.6301 | 12 | 5235.2602 | 16
2227.2787 | 10 | 4454.5573 | 16
2407.488 | 10 | 4814.9761 | 16
2508.3577 | 12 | 5016.7154 | 16
2624.9016 | 12 | 5249.8033 | 16
2111.5713 | 10 | 4223.1426 | 14
2305.4296 | 10 | 4610.8591 | 16
2491.2746 | 10 | 4982.5492 | 16
2766.6299 | 12 | 5533.2599 | 16
3069.239 | 12 | 6138.4781 | 18
3426.3556 | 12 | 6852.7113 | 18
2867.819 | 12 | 5735.638 | 18
3379.8685 | 12 | 6759.737 | 18
3737.7603 | 14 | 7475.5206 | 20
3875.064 | 14 | 7750.128 | 20
4004.1439 | 14 | 8008.2879 | 20
4295.2175 | 16 | 8590.4351 | 20
4595.0968 | 16 | 9190.1937 | 24
4656.6379 | 16 | 9313.2758 | 24
4664.6626 | 16 | 9329.3252 | 24
3448.9864 | 12 | 6897.9727 | 18
3639.5425 | 14 | 7279.085 | 20
4042.4929 | 14 | 8084.9858 | 20
4332.4218 | 16 | 8664.8435 | 20
5072.7199 | 16 | 10145.4398 | 24
5521.0639 | 16 | 11042.1279 | 24
5727.2058 | 18 | 11454.4117 | 24
90.8476 | 2.5 | 272.5428 | 4
106.5592 | 2.5 | 319.6775 | 4
145.3387 | 3 | 436.016 | 5
167.6172 | 3 | 502.8515 | 5
188.3547 | 3 | 565.064 | 5
202.4879 | 3 | 607.4636 | 5
102.972 | 2.5 | 308.9159 | 4
116.1429 | 2.5 | 348.4288 | 4
133.8158 | 3 | 401.4475 | 5
150.196 | 3 | 450.5881 | 5
177.561 | 3 | 532.683 | 5
194.9972 | 3 | 584.9917 | 5
230.1371 | 4 | 690.4113 | 6
242.8034 | 4 | 728.4101 | 6
178.5455 | 3 | 535.6365 | 5
208.9617 | 3 | 626.885 | 5
260.8895 | 4 | 782.6684 | 6
297.3228 | 4 | 891.9684 | 6
273.669 | 4 | 821.0071 | 6
321.881 | 4 | 965.6429 | 8
360.1978 | 4 | 1080.5933 | 8
376.0572 | 4 | 1128.1715 | 8
261.6739 | 4 | 785.0216 | 6
299.9456 | 4 | 899.8369 | 6
365.149 | 4 | 1095.4471 | 8
403.7936 | 5 | 1211.3809 | 8
402.7736 | 5 | 1208.3209 | 8
183.5282 | 3 | 550.5845 | 5
235.9056 | 4 | 707.7169 | 6
254.5738 | 4 | 763.7214 | 6
278.649 | 4 | 835.9471 | 6
302.5651 | 4 | 907.6952 | 6
278.138 | 4 | 834.4139 | 6
343.952 | 4 | 1031.8561 | 8
398.9817 | 4 | 1196.9451 | 8
427.0782 | 5 | 1281.2345 | 8
374.2437 | 4 | 1122.7312 | 8
422.9151 | 5 | 1268.7454 | 8
479.4087 | 5 | 1438.226 | 8
318.8997 | 4 | 956.6991 | 8
359.467 | 4 | 1078.4011 | 8
413.6934 | 5 | 1241.0803 | 8
469.9181 | 5 | 1409.7542 | 8
576.7129 | 5 | 1730.1386 | 10
637.6666 | 5 | 1912.9998 | 10
669.3599 | 6 | 2008.0797 | 10
685.5374 | 6 | 2056.6121 | 10
487.2856 | 5 | 1461.8568 | 8
573.2974 | 5 | 1719.8922 | 10
666.5942 | 6 | 1999.7825 | 10
598.5182 | 5 | 1795.5546 | 10
672.8213 | 6 | 2018.4638 | 10
735.3325 | 6 | 2205.9974 | 10
787.4175 | 6 | 2362.2524 | 10
832.83 | 6 | 2498.4899 | 10
541.7729 | 5 | 1625.3186 | 10
534.0678 | 5 | 1602.2035 | 10
695.2568 | 6 | 2085.7705 | 10
724.1837 | 6 | 2172.551 | 10
864.0628 | 6 | 2592.1883 | 12
924.6022 | 6 | 2773.8066 | 12
1036.8753 | 8 | 3110.626 | 12
1098.4714 | 8 | 3295.4143 | 12
877.0156 | 6 | 2631.0468 | 12
948.7162 | 6 | 2846.1487 | 12
981.9574 | 8 | 2945.8722 | 12
1058.92 | 8 | 3176.7601 | 12
812.9455 | 6 | 2438.8364 | 10
894.4426 | 6 | 2683.3277 | 12
958.5264 | 8 | 2875.5792 | 12
1092.3955 | 8 | 3277.1865 | 12
1108.1578 | 8 | 3324.4733 | 12
1179.7044 | 8 | 3539.1131 | 12
1257.8884 | 8 | 3773.6651 | 14
1397.6463 | 8 | 4192.9389 | 14
1556.5458 | 8 | 4669.6374 | 16
1658.4722 | 10 | 4975.4165 | 16
1749.9638 | 10 | 5249.8913 | 16
840.0118 | 6 | 2520.0353 | 12
912.3919 | 6 | 2737.1757 | 12
963.4895 | 8 | 2890.4686 | 12
1003.339 | 8 | 3010.017 | 12
1234.2559 | 8 | 3702.7677 | 14
1338.3397 | 8 | 4015.019 | 14
1409.7542 | 8 | 4229.2626 | 14
1493.981 | 8 | 4481.9431 | 16
1550.69 | 8 | 4652.0699 | 16
1352.693 | 8 | 4058.0791 | 14
1398.703 | 8 | 4196.109 | 14
1508.9068 | 8 | 4526.7203 | 16
1674.3665 | 10 | 5023.0996 | 16
1200.4144 | 8 | 3601.2433 | 14
1283.8269 | 8 | 3851.4807 | 14
1416.7849 | 8 | 4250.3547 | 16
1508.8665 | 8 | 4526.5994 | 16
1598.8017 | 8 | 4796.4052 | 16
1689.4197 | 10 | 5068.259 | 16
2092.9884 | 10 | 6278.9651 | 18
2346.9884 | 10 | 7040.9653 | 18
2529.5219 | 12 | 7588.5656 | 20
2703.7978 | 12 | 8111.3933 | 20
2169.9766 | 10 | 6509.9297 | 18
2284.2526 | 10 | 6852.7577 | 18
2385.0423 | 10 | 7155.1269 | 20
2493.7612 | 10 | 7481.2836 | 20
2617.6301 | 12 | 7852.8904 | 20
2227.2787 | 10 | 6681.836 | 18
2407.488 | 10 | 7222.4641 | 20
2508.3577 | 12 | 7525.0732 | 20
2624.9016 | 12 | 7874.7049 | 20
2111.5713 | 10 | 6334.7139 | 18
2305.4296 | 10 | 6916.2887 | 18
2491.2746 | 10 | 7473.8238 | 20
2766.6299 | 12 | 8299.8898 | 20
3069.239 | 12 | 9207.7171 | 24
3426.3556 | 12 | 10279.0669 | 24
2867.819 | 12 | 8603.4569 | 20
3379.8685 | 12 | 10139.6056 | 24
3737.7603 | 14 | 11213.2809 | 24
3875.064 | 14 | 11625.1919 | 24
4004.1439 | 14 | 12012.4318 | 24
4295.2175 | 16 | 12885.6526 | 24
4595.0968 | 16 | 13785.2905 | 24
4656.6379 | 16 | 13969.9138 | 24
4664.6626 | 16 | 13993.9878 | 24
3448.9864 | 12 | 10346.9591 | 24
3639.5425 | 14 | 10918.6274 | 24
4042.4929 | 14 | 12127.4788 | 24
4332.4218 | 16 | 12997.2653 | 24
5072.7199 | 16 | 15218.1598 | 24
5521.0639 | 16 | 16563.1918 | 24
5727.2058 | 18 | 17181.6175 | 24
90.8476 | 2.5 | 363.3904 | 4
106.5592 | 2.5 | 426.2366 | 5
145.3387 | 3 | 581.3546 | 5
167.6172 | 3 | 670.4687 | 6
188.3547 | 3 | 753.4187 | 6
202.4879 | 3 | 809.9515 | 6
102.972 | 2.5 | 411.8879 | 5
116.1429 | 2.5 | 464.5717 | 5
133.8158 | 3 | 535.2633 | 5
150.196 | 3 | 600.7841 | 5
177.561 | 3 | 710.244 | 6
194.9972 | 3 | 779.989 | 6
230.1371 | 4 | 920.5484 | 6
242.8034 | 4 | 971.2134 | 8
178.5455 | 3 | 714.1819 | 6
208.9617 | 3 | 835.8467 | 6
260.8895 | 4 | 1043.5578 | 8
297.3228 | 4 | 1189.2912 | 8
273.669 | 4 | 1094.6762 | 8
321.881 | 4 | 1287.5239 | 8
360.1978 | 4 | 1440.7911 | 8
376.0572 | 4 | 1504.2286 | 8
261.6739 | 4 | 1046.6955 | 8
299.9456 | 4 | 1199.7825 | 8
365.149 | 4 | 1460.5961 | 8
403.7936 | 5 | 1615.1746 | 10
402.7736 | 5 | 1611.0945 | 10
183.5282 | 3 | 734.1127 | 6
235.9056 | 4 | 943.6226 | 6
254.5738 | 4 | 1018.2952 | 8
278.649 | 4 | 1114.5962 | 8
302.5651 | 4 | 1210.2603 | 8
278.138 | 4 | 1112.5518 | 8
343.952 | 4 | 1375.8081 | 8
398.9817 | 4 | 1595.9268 | 8
427.0782 | 5 | 1708.3126 | 10
374.2437 | 4 | 1496.975 | 8
422.9151 | 5 | 1691.6605 | 10
479.4087 | 5 | 1917.6347 | 10
318.8997 | 4 | 1275.5988 | 8
359.467 | 4 | 1437.8681 | 8
413.6934 | 5 | 1654.7738 | 10
469.9181 | 5 | 1879.6723 | 10
576.7129 | 5 | 2306.8515 | 10
637.6666 | 5 | 2550.6665 | 12
669.3599 | 6 | 2677.4396 | 12
685.5374 | 6 | 2742.1495 | 12
487.2856 | 5 | 1949.1425 | 10
573.2974 | 5 | 2293.1896 | 10
666.5942 | 6 | 2666.3766 | 12
598.5182 | 5 | 2394.0728 | 10
672.8213 | 6 | 2691.2851 | 12
735.3325 | 6 | 2941.3299 | 12
787.4175 | 6 | 3149.6699 | 12
832.83 | 6 | 3331.3199 | 12
541.7729 | 5 | 2167.0915 | 10
534.0678 | 5 | 2136.2714 | 10
695.2568 | 6 | 2781.0273 | 12
724.1837 | 6 | 2896.7347 | 12
864.0628 | 6 | 3456.2511 | 12
924.6022 | 6 | 3698.4088 | 14
1036.8753 | 8 | 4147.5013 | 14
1098.4714 | 8 | 4393.8858 | 16
877.0156 | 6 | 3508.0625 | 12
948.7162 | 6 | 3794.8649 | 14
981.9574 | 8 | 3927.8296 | 14
1058.92 | 8 | 4235.6802 | 14
812.9455 | 6 | 3251.7819 | 12
894.4426 | 6 | 3577.7702 | 14
958.5264 | 8 | 3834.1056 | 14
1092.3955 | 8 | 4369.582 | 16
1108.1578 | 8 | 4432.631 | 16
1179.7044 | 8 | 4718.8174 | 16
1257.8884 | 8 | 5031.5535 | 16
1397.6463 | 8 | 5590.5852 | 18
1556.5458 | 8 | 6226.1832 | 18
1658.4722 | 10 | 6633.8887 | 18
1749.9638 | 10 | 6999.8551 | 18
840.0118 | 6 | 3360.047 | 12
912.3919 | 6 | 3649.5676 | 14
963.4895 | 8 | 3853.9581 | 14
1003.339 | 8 | 4013.356 | 14
1234.2559 | 8 | 4937.0235 | 16
1338.3397 | 8 | 5353.3587 | 16
1409.7542 | 8 | 5639.0168 | 18
1493.981 | 8 | 5975.9242 | 18
1550.69 | 8 | 6202.7599 | 18
1352.693 | 8 | 5410.7721 | 16
1398.703 | 8 | 5594.812 | 18
1508.9068 | 8 | 6035.6271 | 18
1674.3665 | 10 | 6697.4661 | 18
1200.4144 | 8 | 4801.6577 | 16
1283.8269 | 8 | 5135.3076 | 16
1416.7849 | 8 | 5667.1396 | 18
1508.8665 | 8 | 6035.4659 | 18
1598.8017 | 8 | 6395.207 | 18
1689.4197 | 10 | 6757.6787 | 18
2092.9884 | 10 | 8371.9535 | 20
2346.9884 | 10 | 9387.9538 | 24
2529.5219 | 12 | 10118.0875 | 24
2703.7978 | 12 | 10815.191 | 24
2169.9766 | 10 | 8679.9063 | 20
2284.2526 | 10 | 9137.0102 | 24
2385.0423 | 10 | 9540.1692 | 24
2493.7612 | 10 | 9975.0448 | 24
2617.6301 | 12 | 10470.5205 | 24
2227.2787 | 10 | 8909.1146 | 24
2407.488 | 10 | 9629.9521 | 24
2508.3577 | 12 | 10033.4309 | 24
2624.9016 | 12 | 10499.6065 | 24
2111.5713 | 10 | 8446.2852 | 20
2305.4296 | 10 | 9221.7182 | 24
2491.2746 | 10 | 9965.0984 | 24
2766.6299 | 12 | 11066.5198 | 24
3069.239 | 12 | 12276.9561 | 24
3426.3556 | 12 | 13705.4225 | 24
2867.819 | 12 | 11471.2759 | 24
3379.8685 | 12 | 13519.4741 | 24
3737.7603 | 14 | 14951.0411 | 24
3875.064 | 14 | 15500.2559 | 24
4004.1439 | 14 | 16016.5758 | 24
4295.2175 | 16 | 17180.8701 | 24
4595.0968 | 16 | 18380.3874 | 24
4656.6379 | 16 | 18626.5517 | 24
4664.6626 | 16 | 18658.6504 | 24
3448.9864 | 12 | 13795.9455 | 24
3639.5425 | 14 | 14558.1699 | 24
4042.4929 | 14 | 16169.9717 | 24
4332.4218 | 16 | 17329.687 | 24
5072.7199 | 16 | 20290.8797 | 24
5521.0639 | 16 | 22084.2557 | 24
5727.2058 | 18 | 22908.8234 | 24